## COVER
PROJECT QUALITY PLAN (PQP)
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249
Project-Specific QA/QC, Special Inspection & Statutory Sign-Off Plan
A1 — PROJECT OVERVIEW
Project Name | SaunaLounge
Project Location | 45 South 3rd Street, Ground Floor, Brooklyn, NY 11249 — within The 360 Wythe Condominium
Project Type | Ground-floor interior tenant fitout — 5,783 SF wellness / spa (sauna, cold plunge, pool, locker rooms, lounge, bar, kitchen)
Owner / Client | Saunalounge, LLC (Teal Development / JLKing Consulting) | Client Rep: Jeffrey Aser, Teal Development Partners — 914.319.7493, jeff@tealdevelopment.com
Landlord / Condominium | FREEWYTHE, LLC ¦ The 360 Wythe Condominium Board of Managers
Construction Manager | Affect Build, LLC — 389 5th Avenue, Suite 504, New York, NY 10016
Contract Type | AIA Document A104™–2017, Standard Abbreviated Form, Exhibits A–I
Contract Sum | $3,526,451.50 (incl. $247,968.00 Limited Work / early-release HVAC)
Contract Executed | Owner 6/19/2026 ¦ Contractor 6/22/2026
Project Duration | 6/19/2026 – 1/6/2027 (144 calendar days; 3 weeks preconstruction + 26 weeks on site)
Target Substantial Completion | 2026-12-21
Affect Build Job Number
DOB Job / Filing Number
PROJECT QUALITY TEAM (Q-TEAM)
Project Manager | Illeana Aguire | QA owner: ensures submittals / shop drawings approved prior to procurement and installation; engages testing and inspection agencies; issues NCRs
Site Superintendent | Nicholas Scarmacca | QC owner in the field: on-site QC lead; coordinates inspections 48–72 hrs in advance; verifies readiness; maintains the inspector sign-in log
Assistant Project Manager | Hugh McDonagh | Maintains submittal, ITP and inspection registers in Procore; tracks report receipt and closure
Director of Construction | Enda Forrey | Accountability: verifies benchmarks are established and documented, quality records maintained and procedures followed; escalation point for repeat deficiencies
Architect of Record | Colberg Architecture | Required at First Work Review for Tier 3 / Tier 4 DFOWs
MEP / FP Engineer | Collectif | TR8 mechanical / energy code special inspections
Special Inspections Agency | CodeGreen Inspection (CGI) | TR1 / TR2 / TR3 / TR8 · Matrix ref. 2026-0401 · 12 budgeted site visits · allow min. 2–3 days to schedule
Testing Laboratory |  | Concrete testing — to be engaged; enter laboratory name
Commissioning Agent |  | Owner's CA if appointed
Owner's Separate Trades | Pool shell, sauna assemblies, cold plunge basin (Contract §12.4) | Affect Build provides rough-in, coordination and finish trades only; inspects its own interfaces
GOVERNING DOCUMENTS & HIERARCHY
1 | Contract Documents — AIA A104–2017 and Exhibits A–I | Order of precedence per CMP §2.2
2 | Vision Zero QA/QC Playbook v2.0 (governing quality document) | Supersedes all prior QA/QC guidance
3 | Construction Management Plan — SaunaLounge (DRAFT) | Sections 7, 8, 9, 12, 19, 20
4 | Affect Trainual SOPs — Quality Management; Submittals & Inspections | Read alongside the Playbook
5 | NYC Building Code Chapter 17 (Special Inspections) and Chapter 33 | TR1 / TR8 filings via DOB NOW
6 | NYC DOH Pool / Spa requirements; FDNY rules; NFPA 13 and NFPA 72 | Life safety and pool sign-off
QUALITY FRAMEWORK — HOW THIS WORKBOOK IS USED
Four Phases of Control | Every DFOW: Phase 1 Preparatory → Phase 2 Work Readiness → Phase 3 First Work Review → Phase 4 Follow-Up | Tracked on the DFOW Risk Register
DFOW Risk Tiers | Tier 4 Critical (daily follow-up, dual sign-off) · Tier 3 High (every other day, A/E at First Work Review) · Tier 2 Moderate (weekly) · Tier 1 Low (at completion) | Tier drives inspection intensity
Hold vs Witness Points | HOLD — work stops until signed off, no exceptions. WITNESS — 48 hrs notice; work may proceed if witness does not attend after written notice | Defined per test on the ITP
Benchmark Hold Points (CMP §8.4) | Pre-cover before drywall · Waterproofing before backfill at pool equipment room · Above-ceiling before tile / grid close-up · Interface at Owner's pool / sauna assemblies | Non-negotiable
Non-Conformance | Seven-step NCR process; NCRs closed before the next progress billing is approved | NCR Log tab
Punch | Four phases: Trade Self-Punch → Affect Build Review → Owner / A/E Walk → Back Punch. Zero Punch is the objective | Punch & RCL Log tab
System of Record | Procore is the mandatory system of record. This workbook is the project control and reporting mirror | Playbook Quality Policy
WORKBOOK CONTENTS
DASHBOARD | Single-page roll-up of all Quality, Special and Statutory inspection status
DFOW Risk Register | 32 SaunaLounge DFOWs with risk tier, hold points, special inspection requirement and phase tracking
ITP | Inspection & Testing Plan — 31 tests with acceptance criteria and Hold / Witness designation
Path to TCO | 45 sequenced statutory gates from permit issuance to Certificate of Occupancy
Path to Fire Alarm | 23-step FDNY Letter of Approval pathway
Statutory Inspections | DOB · FDNY · DOH · DEP · Con Edison / National Grid inspection and approval log
Special Inspections | NYC BC Chapter 17 — TR1 / TR2 / TR3 / TR8 log with hold points and report tracking | CodeGreen (CGI) budgeted programme block at rows 48-60
Inspector Sign-In | Mandatory physical inspector sign-in log (digital mirror)
Commissioning | Equipment-by-equipment start-up, FPT, TAB, training and turnover matrix
Submittals & Mockups | Submittal, sample and mock-up register including 8 project mock-ups
Checklist / Sample Size | Existing DFOW checklist matrix and ANSI/ASQ inspection sample size chart
NCR Log | Observation / Non-Conformance Report log — seven-step process
Punch & RCL Log | Punch list and Rolling Completion List with aging escalation
Trade QC Checklists | 26 project-specific trade checklist tabs, each with Q-Team sign-off block
DOH Checklist | NYC DOHMH first-pass compliance checklist — 101 items across pool/spa (NYS Subpart 6-1, Health Code Art. 165) and food service (Art. 81), with responsibility split against Owner's Separate Trades

## DASHBOARD
QA/QC MASTER TRACKER — SAUNALOUNGE, 45 SOUTH 3RD STREET
Comprehensive roll-up of Quality, Special and Statutory inspections. All figures are live formulas driven by the register tabs — update the registers, not this page.
A. PROGRAMME READINESS — STATUTORY, SPECIAL & QUALITY REGISTERS
Register | Total | Complete / Passed | Open / Outstanding | Failed / Blocked | % Complete | Where to update
Path to TCO — statutory gates | 46 | 0 | 46 | 0 | 0% | Path to TCO tab
Path to Fire Alarm — FDNY LOA steps | 23 | 0 | 23 | 0 | 0% | Path to Fire Alarm tab
Statutory inspections & agency approvals | 24 | 0 | 24 | 0 | 0% | Statutory Inspections tab
Special inspections (NYC BC Ch.17 — TR forms) | 36 | 0 | 36 | 0 | 0% | Special Inspections tab
ITP — tests & inspections | 31 | 0 | 31 | 0 | 0% | ITP tab
Commissioning & turnover — systems accepted | 38 | 0 | 38 | 0 | 0% | Commissioning tab
Submittals, samples & mock-ups | 39 | 0 | 39 | 0 | 0% | Submittals & Mockups tab
DFOW register — Phase 4 follow-up complete | 32 | 0 | 32 | 0 | 0% | DFOW Risk Register tab
Trade QC checklists — line items | 625 | 0 | 625 | 0 | 0% | 26 trade checklist tabs
DOH compliance checklist (pool / spa + Article 81 food service) | 101 | 0 | 101 | 0 | 0% | DOH Checklist tab — first pass; numeric criteria require confirmation by the Owner's DOH consultant
B. CRITICAL DATES & QUALITY EXCEPTIONS
Metric | Value |  |  |  |  | Standard / Action
Target Substantial Completion | 2026-12-21 |  |  |  |  | Per Exhibit E — CMP §2.1
Calendar days remaining to Substantial Completion | 129 |  |  |  |  | Live countdown
Latest permissible FDNY fire alarm witness test date | 2026-12-07 |  |  |  |  | CMP §20.1 — minimum 2 weeks before SC to allow re-tests
TCO readiness | 0% |  |  |  |  | All gates must reach Complete before TCO filing
Open NCRs / corrective actions | 0 |  |  |  |  | Target ZERO. NCRs must close before the next progress billing is approved
NCRs past target close date | 0 |  |  |  |  | Escalate: 3-5 working days standard; Tier 4 within 72 hours
Average days to close an NCR | — |  |  |  |  | Tracked weekly at Q-Team meeting
Open punch / RCL items | 0 |  |  |  |  | Zero Punch is the objective (Playbook A9)
Open punch items with life-safety / occupancy impact | 0 |  |  |  |  | Correct within 48 hours
Punch items aged over 7 days | 0 |  |  |  |  | Beyond 5 days escalate to trade PM; beyond 7 days to trade executive
Inspector sign-in entries recorded | 0 |  |  |  |  | Mandatory for every DOB / FDNY / DOH / SIA / lab visit
Tier 3 & Tier 4 DFOWs (elevated control) | 17 |  |  |  |  | Daily / every-other-day follow-up required
CodeGreen (CGI) budgeted special inspection visits remaining | 12 |  |  |  |  | 12 visits budgeted per CGI matrix 2026-0401. Log each visit used on the Special Inspections tab (row 50-59)
C. TRADE QC CHECKLIST ROLL-UP — 26 PROJECT-SPECIFIC CHECKLISTS
Trade Checklist Tab | DFOW Ref | Risk Tier | Checklist Items | Pass | Fail | % Complete
Excavation | D-08 | 3 | 19 | 0 | 0 | 0%
Concrete Formwork | D-07 | 3 | 25 | 0 | 0 | 0%
Conc Reinforcement | D-07 | 3 | 26 | 0 | 0 | 0%
CIP Concrete | D-07 | 3 | 28 | 0 | 0 | 0%
Precast Concrete | D-07 | 3 | 21 | 0 | 0 | 0%
Unit Masonry | D-19 | 2 | 31 | 0 | 0 | 0%
Metal Deck | D-18 | 2 | 30 | 0 | 0 | 0%
Slab on Grade | D-07 | 3 | 19 | 0 | 0 | 0%
Slab on Deck | D-07 | 3 | 13 | 0 | 0 | 0%
Waterproofing | D-01 / D-02 | 4 | 27 | 0 | 0 | 0%
Drywall Framing | D-18 | 2 | 28 | 0 | 0 | 0%
Drywall Board | D-20 | 2 | 28 | 0 | 0 | 0%
Firestopping | D-15 | 3 | 22 | 0 | 0 | 0%
Metal Frames | D-21 | 2 | 17 | 0 | 0 | 0%
Metal Doors | D-21 | 2 | 25 | 0 | 0 | 0%
Doors & Hardware | D-21 | 2 | 22 | 0 | 0 | 0%
Tile & Stone | D-14 | 3 | 24 | 0 | 0 | 0%
Resilient Flooring | D-27 | 2 | 28 | 0 | 0 | 0%
ACT Ceilings | D-25 | 2 | 20 | 0 | 0 | 0%
Millwork & Casework | D-16 | 3 | 24 | 0 | 0 | 0%
Painting | D-28 | 1 | 19 | 0 | 0 | 0%
Electrical | D-05 | 4 | 25 | 0 | 0 | 0%
Plumbing | D-06 / D-13 | 4 | 26 | 0 | 0 | 0%
HVAC & Ductwork | D-10 / D-11 | 3 | 26 | 0 | 0 | 0%
Fire Sprinkler | D-04 | 4 | 24 | 0 | 0 | 0%
Fire Alarm | D-03 | 4 | 28 | 0 | 0 | 0%
TOTAL — ALL TRADE CHECKLISTS |  |  | 625 | 0 | 0 | 0%
Formulas:
Total = [Total, row above]-TODAY()

## Project Identifiers
SAUNALOUNGE — PROJECT IDENTIFIERS & Q-TEAM RESPONSIBILITY MATRIX
45 South 3rd Street, Ground Floor, Brooklyn NY 11249 ¦ Affect Build, LLC ¦ Precon tool used to fix roles and responsibilities of the Q-Team. The Q-Team then collaboratively populates the QA activity matrix below, which drives the Checklist, NCR, Control Samples, Mock-Ups, Punchlist Walks and Monthly QA Reviews.
A. Q-TEAM MEMBERS & RESPONSIBILITIES
Role | Name
Project Manager | Illeana Aguire
Site Superintendent | Nicholas Scarmacca
Assistant Project Manager | Hugh McDonagh
Director of Construction | Enda Forrey
B. QA/QC ACTIVITY & GOVERNANCE MATRIX
Type | Requirement | Tool / Format | Sign-Off | Stored Where
First Delivery Inspection | HVAC equipment (RT-1, PDU-1, ERV-1/2, AC-1 to AC-5) Switchgear & panels (SWBD-1, MP-1, KP-1, LP-1, RP-1) Rheem tankless water heaters + ST-120 tank Waterproofing membrane system Tile & stone (TL-1, TL-2, TL-3) Millwork & casework Doors, frames & hardware Sprinkler heads (87) Fire alarm devices (FACP / RAN) ACT ceiling panels & grid Plumbing fixtures (incl. Kohler substitution) Lighting fixtures & controls Glass block Wood flooring | Procore Inspection Checklist | Superintendent / Trade Partner | Procore — Inspections
Benchmark Inspection | Wet-area waterproofing (locker rooms, showers, pool deck) Waterproofing interface at Owner's pool / sauna assemblies Pool equipment room slab & CIP concrete Metal stud framing (barrel vault, soffits) GWB Level 5 skim finish Tile & stone (each type) Polished / sealed concrete at BOH Firestopping (typical rated penetration) Millwork (locker unit, reception desk) Doors & hardware Painting & wall coverings ACT ceiling grid MEP rough-in (pre-cover) Above-ceiling close-up | Procore Inspection + Benchmark Form | Q-Team / Trade Partner | Procore — Benchmarks / PDF binder
Mock-Up Review | Tile & stone — pool deck / shower assembly with waterproofing transition GWB Level 5 skim finish panel Locker unit & reception desk first article Polished / sealed concrete floor sample (BOH) Paint & wall covering sample area Glass block wall panel Firestopping typical UL penetration Wood flooring accent panel (pool / lounge) | In-field physical sample + photo log | Q-Team / Architect / Client Rep | Onsite + Procore Photo Documentation
Non-Conformance Report (NCR) | Documented deviation from plans/specs or unacceptable workmanship | Procore Observations Tool | Superintendent / PM | Procore — Observations
Control Samples | Keep one sample of each approved material onsite | Stored physically in labeled plastic box | QA/QC Manager | Site Office Sample Bin
Punchlist Walks | Final completion walkthrough for trade and general scopes | Procore Punchlist Tool | Q-Team / Design Team / Client Rep | Procore — Punchlists
Monthly QA Review | Review completed vs. missed benchmarks | Internal Project Schedule / QA Log | PM / Superintendent | Project Folder / QA Dashboard

## DFOW Risk Register
SAUNALOUNGE — DFOW RISK & QUALITY GOVERNANCE MATRIX (Playbook App. D-B)
45 South 3rd Street, Ground Floor, Brooklyn NY 11249 ¦ Affect Build, LLC ¦ Tier drives inspection intensity, documentation level and Q-Team attendance
DFOW ID | DFOW / Definable Feature of Work | Tier | Risk Level | Insp. Intensity / Follow-Up Freq. | CSI Div / Spec | Zone / Location | Responsible Trade Partner | Affect Lead (PM / Super) | Mock-Up Req'd | Hold / Witness Points | Special Insp. Req'd (TR) | Ph.1 Preparatory | Ph.2 Work Readiness | Ph.3 First Work Review | Ph.4 Follow-Up Status | Notes
D-01 | Wet-area waterproofing — pool deck, locker rooms, showers, kitchen | 4 | Critical | Daily follow-up; dual sign-off; QA/QC Mgr at all hold points | 2009-03-07 | Zone A & B wet areas |  | N. Scarmacca (Super) | Yes | HOLD — before tile/topping cover-up | TR12/13-adjacent
D-02 | Waterproofing interface w/ Owner's pool shell, sauna & cold plunge assemblies | 4 | Critical | Daily follow-up; dual sign-off; QA/QC Mgr at all hold points | 7 | Pool room (Zone B) |  | N. Scarmacca (Super) / I. Aguire (PM) | Yes | HOLD — joint interface inspection w/ Owner vendor | TR12/13-adjacent
D-03 | Fire Alarm system — FACP, RAN, initiating / notification devices | 4 | Critical | Daily follow-up; dual sign-off; QA/QC Mgr at all hold points | 28 31 00 | Whole premises |  | I. Aguire (PM) | No | HOLD — 100% device pre-test; WITNESS — FDNY acceptance | TR1
D-04 | Fire Sprinkler & standpipe — 87 new heads, main & branch | 4 | Critical | Daily follow-up; dual sign-off; QA/QC Mgr at all hold points | 21 13 00 | Whole premises |  | N. Scarmacca (Super) | No | HOLD — hydrostatic 200 psi / 2 hr (DOB witness); WITNESS — FDNY flow test | TR1
D-05 | Electrical service, switchgear & panels MP-1, KP-1, LP-1, RP-1, SWBD-1 | 4 | Critical | Daily follow-up; dual sign-off; QA/QC Mgr at all hold points | 26 20 00 | Elec. room / Zones A & B |  | I. Aguire (PM) | No | HOLD — pre-energisation inspection & megger | TR - Electrical
D-06 | Gas piping & elevated-pressure gas service connection | 4 | Critical | Daily follow-up; dual sign-off; QA/QC Mgr at all hold points | 22 11 00 | Kitchen / mech. |  | N. Scarmacca (Super) | No | HOLD — 10 psi / 15 min pressure test (DOB witness) | DOB Plumbing
D-07 | Pool equipment room slab & CIP concrete | 3 | High | Every-other-day follow-up; A/E at First Work Review | 03 30 00 | Pool equipment room |  | N. Scarmacca (Super) | No | HOLD — pre-pour rebar/embeds; WITNESS — each pour | TR2 / TR3
D-08 | Excavation & support of excavation — pool equipment room (150 CY) | 3 | High | Every-other-day follow-up; A/E at First Work Review | 31 20 00 | Pool equipment room |  | N. Scarmacca (Super) | No | HOLD — SOE verification before excavation | TR4 / TR5
D-09 | Domestic hot water — 4x Rheem tankless + ST-120 storage tank | 3 | High | Every-other-day follow-up; A/E at First Work Review | 22 33 00 | Mech. room |  | I. Aguire (PM) | No | HOLD — combustion test before DOB Boiler Unit insp. | DOB Boiler
D-10 | HVAC equipment — RT-1, PDU-1, ERV-1/2, AC-1 to AC-5, MUA-1, KEF-1 | 3 | High | Every-other-day follow-up; A/E at First Work Review | 23 00 00 | Roof / Zones A & B |  | I. Aguire (PM) | No | WITNESS — startup & functional performance test | TR8
D-11 | Ductwork Zones A & B incl. duct pressure testing | 3 | High | Every-other-day follow-up; A/E at First Work Review | 23 31 00 | Zones A & B |  | N. Scarmacca (Super) | No | HOLD — duct pressure test before ceiling close-up | TR8
D-12 | Refrigerant piping — ACCU-1 / ACCU-2 reconnect, ACCU-3 new | 3 | High | Every-other-day follow-up; A/E at First Work Review | 23 23 00 | Roof / Zone A |  | I. Aguire (PM) | No | HOLD — pressure/vacuum test before charge | —
D-13 | Plumbing rough-in — CW / HW / sanitary / waste / vent | 3 | High | Every-other-day follow-up; A/E at First Work Review | 22 10 00 | Zones A & B |  | N. Scarmacca (Super) | No | HOLD — pre-cover inspection before GWB | DOB Plumbing
D-14 | Tile & stone — pool floors, locker/shower, lounge/bar, kitchen, ADA restroom | 3 | High | Every-other-day follow-up; A/E at First Work Review | 09 30 00 | Zones A & B |  | N. Scarmacca (Super) | Yes | HOLD — mock-up sign-off before production | —
D-15 | Firestopping — all rated penetrations | 3 | High | Every-other-day follow-up; A/E at First Work Review | 07 84 00 | Whole premises |  | N. Scarmacca (Super) | Yes | HOLD — before cover-up | TR - Firestop
D-16 | Millwork & casework — lockers, reception, bar, coat check, kitchen, kiosk | 3 | High | Every-other-day follow-up; A/E at First Work Review | 06 40 00 | Zones A & B |  | I. Aguire (PM) | Yes | HOLD — shop visit / first article review | —
D-17 | Roof penetrations, curbs & flashing at RTU-1 and roof equipment | 3 | High | Every-other-day follow-up; A/E at First Work Review | 07 50 00 | Roof |  | N. Scarmacca (Super) | No | HOLD — flood / water test before close-up | —
D-18 | Metal stud framing Zones A & B, barrel vault, soffits & dropped ceilings | 2 | Moderate | Weekly follow-up; Superintendent-led | 09 22 00 | Zones A & B |  | N. Scarmacca (Super) | No | HOLD — layout & framing check before rough-in | —
D-19 | Glass block wall framing & installation | 2 | Moderate | Weekly follow-up; Superintendent-led | 04 23 00 | Zone A |  | N. Scarmacca (Super) | Yes | First Work Review | —
D-20 | GWB hang, tape, finish & Level 5 skim coat | 2 | Moderate | Weekly follow-up; Superintendent-led | 09 29 00 | Zones A & B |  | N. Scarmacca (Super) | Yes | HOLD — pre-cover sign-off before board | —
D-21 | Doors, frames & hardware | 2 | Moderate | Weekly follow-up; Superintendent-led | 08 11 00 | Whole premises |  | N. Scarmacca (Super) | No | First Work Review | —
D-22 | Blocking & in-wall backing / anchors | 2 | Moderate | Weekly follow-up; Superintendent-led | 06 10 00 | Zones A & B |  | N. Scarmacca (Super) | No | HOLD — pre-cover inspection | —
D-23 | Low-voltage / AV rough-in | 2 | Moderate | Weekly follow-up; Superintendent-led | 27 00 00 | Zones A & B |  | I. Aguire (PM) | No | HOLD — pre-cover inspection | —
D-24 | Lighting controls & dimming (Exhibit G allowance) | 2 | Moderate | Weekly follow-up; Superintendent-led | 26 09 00 | Zones A & B |  | I. Aguire (PM) | No | WITNESS — controls functional test | —
D-25 | ACT / acoustic ceiling panels & grid | 2 | Moderate | Weekly follow-up; Superintendent-led | 09 51 00 | Zones A & B |  | N. Scarmacca (Super) | No | HOLD — above-ceiling MEP inspection before grid close-up | —
D-26 | Layout & survey control — benchmarks and control lines | 2 | Moderate | Weekly follow-up; Superintendent-led | 01 71 23 | Whole premises |  | N. Scarmacca (Super) | No | HOLD — control sign-off before any trade layout | —
D-27 | Polished / sealed concrete floor at BOH | 2 | Moderate | Weekly follow-up; Superintendent-led | 03 35 00 | BOH (Zone A) |  | N. Scarmacca (Super) | Yes | Mock-up + First Work Review | —
D-28 | Painting & wall coverings | 1 | Low | At completion; Superintendent spot-check | 09 90 00 | Whole premises |  | N. Scarmacca (Super) | Yes | First Work Review | —
D-29 | Wood flooring accent — pool / lounge | 1 | Low | At completion; Superintendent spot-check | 09 64 00 | Zones A & B |  | N. Scarmacca (Super) | Yes | First Work Review | —
D-30 | Bath accessories, toilet partitions & stalls | 1 | Low | At completion; Superintendent spot-check | 10 21 00 | Locker rooms / ADA restroom |  | N. Scarmacca (Super) | No | At completion | —
D-31 | Signage & wayfinding | 1 | Low | At completion; Superintendent spot-check | 10 14 00 | Whole premises |  | I. Aguire (PM) | No | At completion | —
D-32 | Final clean & protection removal | 1 | Low | At completion; Superintendent spot-check | 01 74 00 | Whole premises |  | N. Scarmacca (Super) | No | At completion | —

## ITP
SAUNALOUNGE — INSPECTION & TESTING PLAN (ITP) ¦ Playbook App. D-C
H = HOLD POINT: work must stop; inspection signed off before proceeding — no exceptions. W = WITNESS POINT: Affect Build and/or A/E notified min. 48 hrs in advance; work may proceed if witness does not attend after proper written notice. All reports uploaded to Procore within 24 hrs of receipt.
ITP ID | DFOW Ref | Test / Inspection Activity | Spec / Code Requirement | Test Method / Standard | Acceptance Criteria | Frequency | Responsible Party | H / W | Notice Req'd | Date Performed | Result | Report Ref (Procore) | Status | Report Distribution
T-01 | D-07 | Concrete compressive strength — pool equipment room slab | NYC BC Ch.17 / TR2-TR3 | ASTM C39 cylinder breaks | Meets design f'c at 28 days | Each pour (min. 1 set per 50 CY) | Licensed Testing Laboratory | H | 48 hrs |  |  |  |  | PM, Super, SIA, Architect, Collectif
T-02 | D-07 | Concrete slump, air content & temperature | NYC BC Ch.17 / TR2 | ASTM C143 / C231 / C1064 | Within approved mix design tolerances | Each truck / each pour | Licensed Testing Laboratory | W | 48 hrs |  |  |  |  | PM, Super, SIA
T-03 | D-07 | Pre-pour rebar, embeds & formwork verification | Structural drawings / TR3 | Visual + tape measure vs. shop drawings | Placement, cover and laps per approved shops | Before every pour | Special Inspection Agency | H | 48 hrs |  |  |  |  | PM, Super, SIA, Architect
T-04 | D-08 | Excavation / SOE verification — pool equipment room | NYC BC Ch.33 / TR4-TR5 | Survey + visual vs. approved SOE drawings | Sloped excavation per approved SOE; no undermining | Before and during excavation | Special Inspection Agency | H | 48 hrs |  |  |  |  | PM, Super, SIA
T-05 | D-01 | Wet-area waterproofing flood test — locker rooms, showers, pool deck | Manufacturer's requirements / 07 | Flood test min. 24 hrs, 2 in. head | No loss of head; no evidence of leakage | Each wet area, before cover-up | Waterproofing Subcontractor | H | 48 hrs |  |  |  |  | PM, Super, Architect, Owner
T-06 | D-02 | Interface inspection — Affect waterproofing to Owner's pool / sauna assemblies | Contract §12.4 / manufacturer | Joint visual inspection + photo record | Continuous termination; no gaps at transition | At each interface, before cover-up | N. Scarmacca (Super) + Owner's Pool Vendor | H | 72 hrs |  |  |  |  | PM, Super, Architect, Owner's Vendor
T-07 | D-17 | Roof flood / water test at RTU-1 curbs and penetrations | 07 50 00 / manufacturer | Water test / spray test | No leakage at curbs, flashings or penetrations | Once, after flashing complete | Roofing Subcontractor | H | 48 hrs |  |  |  |  | PM, Super, Architect
T-08 | D-04 | Sprinkler hydrostatic test | NFPA 13 / NYC BC / TR1 | Hydrostatic pressure test | 200 psi held 2 hrs with no loss | Once per system, all new piping | Sprinkler Subcontractor (DOB witness) | H | 72 hrs |  |  |  |  | PM, Super, DOB, FDNY, SIA
T-09 | D-04 | Sprinkler flow test — waterflow & tamper switches | NFPA 13 / FDNY | Flow test at inspector's test connection | Alarm signal within 90 sec; correct pressure | Once, at final acceptance | Sprinkler Subcontractor (FDNY witness) | W | 72 hrs |  |  |  |  | PM, Super, FDNY, SIA
T-10 | D-03 | Fire alarm 100% device pre-test | NFPA 72 / FDNY / TR1 | Point-by-point functional device test | 100% of initiating, signaling & notification devices operate | Once, before FDNY witness test | Fire Alarm Subcontractor | H | 72 hrs |  |  |  |  | PM, Super, Collectif, SIA
T-11 | D-03 | Fire alarm interface test — HVAC damper closure & door hold-open release | NFPA 72 / NYC MC | Functional interface test | All dampers close and hold-opens release on alarm | Once, with pre-test | Fire Alarm + Mechanical Subs | H | 72 hrs |  |  |  |  | PM, Super, Collectif
T-12 | D-03 | FDNY fire alarm witness / acceptance test | FDNY rules / TR1 | FDNY witnessed live device test | FDNY Letter of Approval (LOA) issued | Once (≥2 weeks before 12/21/26) | FDNY Inspector | W | 2 weeks |  |  |  |  | PM, Super, Owner, FDNY, SIA
T-13 | D-03 | Central station / alarm transmission verification | FDNY | Signal transmission test to central station | Signal received and logged by central station | Once, at final acceptance | Fire Alarm Subcontractor | W | 72 hrs |  |  |  |  | PM, Super, FDNY
T-14 | D-06 | Gas piping pressure test | NYC Fuel Gas Code / DOB Plumbing | Air pressure test | 10 psi held 15 min minimum with no loss | Each new gas run | Plumbing Subcontractor (DOB witness) | H | 72 hrs |  |  |  |  | PM, Super, DOB, Collectif
T-15 | D-13 | Plumbing rough-in — water, sanitary & vent inspection | NYC PC / DOB Plumbing | Hydrostatic / air test + DOB inspection | No loss of pressure; DOB sign-off obtained | Each rough-in area, before cover | Plumbing Subcontractor | H | 72 hrs |  |  |  |  | PM, Super, DOB
T-16 | D-09 | Water heater combustion test — 4x Rheem tankless + ST-120 | Manufacturer / NYC MC | Combustion analysis | CO / O2 within manufacturer's limits | Once per unit at startup | Plumbing / Mechanical Sub | H | 48 hrs |  |  |  |  | PM, Super, Collectif, DOB Boiler Unit
T-17 | D-05 | Electrical insulation resistance (megger) & grounding continuity | NETA / NYC EC | Megger + continuity test | Insulation resistance and bonding per NETA / spec | Before energisation of each panel | Electrical Subcontractor | H | 48 hrs |  |  |  |  | PM, Super, Collectif
T-18 | D-05 | Electrical rough & final inspection / Certificate of Electrical Inspection | NYC EC / DOB NOW | DOB electrical inspection | Certificate of Electrical Inspection issued or self-certified | Rough and final | Licensed Electrician / DOB | H | 1 week |  |  |  |  | PM, Super, Owner, DOB
T-19 | D-11 | Duct pressure / leakage test | SMACNA / 23 31 00 / TR8 | SMACNA duct leakage test | Leakage within SMACNA class per spec | Each system, before ceiling close-up | Mechanical Subcontractor | H | 48 hrs |  |  |  |  | PM, Super, Collectif, SIA
T-20 | D-10 | HVAC equipment startup & functional performance test | 23 00 00 / manufacturer | Vendor certified startup + FPT | Operates per design; certified startup report issued | Each unit | Manufacturer / Mechanical Sub | W | 48 hrs |  |  |  |  | PM, Super, Collectif, Owner
T-21 | D-10 | Testing, Adjusting & Balancing (TAB) | 23 05 93 / NEBB or AABC | TAB per specification | Airflows within ±10% of design CFM | Once, whole system | Approved TAB Firm | W | 1 week |  |  |  |  | PM, Super, Collectif, Owner
T-22 | D-10 | Mechanical / energy code compliance special inspection | NYC ECC / TR8 | SIA review + documentation | TR8 signed off by Collectif | At system completion | Collectif (Mech. Engineer) | H | 1 week |  |  |  |  | PM, Super, Owner, DOB, SIA
T-23 | D-12 | Refrigerant piping pressure / vacuum test | 23 23 00 / manufacturer | Pressure & evacuation test | Holds test pressure; vacuum to manufacturer's spec | Each circuit before charging | Mechanical Subcontractor | H | 48 hrs |  |  |  |  | PM, Super, Collectif
T-24 | D-15 | Firestopping inspection — rated penetrations | 07 84 00 / NYC BC Ch.17 | Visual vs. UL listed system | Correct UL system, depth and annular space | Each rated penetration, before cover | Special Inspection Agency | H | 48 hrs |  |  |  |  | PM, Super, SIA, Architect
T-25 | D-25 | Above-ceiling MEP coordination inspection | 01 45 00 / Playbook A5.4 | Joint walk with all MEP trades | All rough-in complete, tested, labelled; access maintained | Each area, before grid close-up | N. Scarmacca (Super) | H | 48 hrs |  |  |  |  | PM, Super, all MEP subs, Architect
T-26 | D-20 | Pre-cover (pre-drywall) inspection | Playbook A5.4 | Joint trade walk + Closure Record D-G | All in-wall work complete, tested and signed by each trade | Each area, before board | N. Scarmacca (Super) | H | 48 hrs |  |  |  |  | PM, Super, all trades, Architect
T-27 | D-14 | Tile & stone mock-up review and sign-off | 09 30 00 | Q-Team mock-up review | Mock-up formally signed off before production | Once per tile type (TL-1, TL-2, TL-3) | Q-Team + Architect + Owner Rep | H | 1 week |  |  |  |  | PM, Super, Architect, Owner
T-28 | D-24 | Lighting controls / dimming functional test | 26 09 00 / Exhibit G | Functional scene & dimming test | All scenes and zones operate per design | Once, whole system | Electrical Subcontractor | W | 48 hrs |  |  |  |  | PM, Super, Architect, Owner
T-29 | D-26 | Layout & survey control verification | 01 71 23 / Trainual Setting Out SOP | Total station / laser verification | Control benchmarks documented and signed off | Before any trade layout | Superintendent + Surveyor | H | 48 hrs |  |  |  |  | PM, Super, all trades
T-30 | — | DEP backflow prevention device test & certification | NYC DEP / 22 11 19 | Certified backflow test | Device passes; DEP certification filed | Once, at completion | Licensed Backflow Tester | H | 1 week |  |  |  |  | PM, Super, Owner, DEP
T-31 | — | DOH Pool / Spa final inspection (Owner's Separate Trades) | NYC DOH / Contract §12.4 | DOH inspector site inspection | DOH Pool/Spa approval issued | Once, before occupancy | NYC DOH / Owner's Pool Vendor | H | 2 weeks |  |  |  |  | PM, Super, Owner, DOH

## Path to TCO
SAUNALOUNGE — PATH TO TCO ¦ Statutory Sign-Off Gate Register
TCO Request is filed via DOB NOW only once ALL of the following are complete: FDNY Fire Alarm LOA · Sprinkler/Standpipe approval · Electrical & Plumbing final certificates · DOH Pool/Spa approval · all Special Inspection (TR) closures. (CMP §20.4)
Target Substantial Completion |  | 2026-12-21 | Total Gates | 46 | Complete | 0 | Outstanding | 46 | TCO Readiness | 0%
Step | Gate / Milestone | Category | Agency / Authority | Prerequisite Step(s) | Responsible | Required Document / Certificate | Target Date | Status | Actual Date | Days to SC | Procore / DOB NOW Ref | Notes
A. PERMITS, FILINGS & PRECONSTRUCTION
A1 | PW1 / PW2 filings approved and work permits issued | DOB | NYC DOB | — | I. Aguire (PM) | Approved PW1, issued PW2 work permit |  | Not Started
A2 | TR1 (Technical Report — Statement of Responsibility) filed and accepted | DOB | NYC DOB / SIA | A1 | I. Aguire (PM) | Accepted TR1 in DOB NOW |  | Not Started
A3 | TR8 (Energy / Mechanical) filed and accepted | DOB | NYC DOB / Collectif | A1 | I. Aguire (PM) | Accepted TR8 in DOB NOW |  | Not Started
A4 | Special Inspection Agency and Testing Laboratory engaged and on record | Internal | Affect Build | A2 | I. Aguire (PM) | Executed agency agreements |  | Not Started
A5 | Physical inspector sign-in logbook established at site entry | Internal | Affect Build | A1 | N. Scarmacca (Super) | Bound logbook on site (see Inspector Sign-In tab) |  | Not Started
A6 | Permit board, site safety and code postings in place | DOB | NYC DOB | A1 | N. Scarmacca (Super) | Photo record of postings |  | Not Started
A7 | CodeGreen (CGI) Preliminary special inspection completed | Special Insp. | CodeGreen Inspection (CGI) | A1,A4 | N. Scarmacca (Super) | CGI Preliminary inspection report |  | Not Started |  |  |  | MUST occur PRIOR TO any work being performed on site (CGI matrix 2026-0401). Allow min. 2-3 days to schedule
B. SPECIAL INSPECTION (TR) CLOSURES — CMP §12.6
B1 | Concrete placement special inspections complete — pool equipment room slab | Special Insp. | Licensed Testing Lab | A2 | N. Scarmacca (Super) | Signed TR2 / TR3 reports, all pours |  | Not Started
B2 | Excavation / SOE special inspections complete | Special Insp. | Special Inspection Agency | A2 | N. Scarmacca (Super) | Signed TR reports |  | Not Started
B3 | Waterproofing (wet-area interface) special inspections complete | Special Insp. | Independent Inspector | A2 | N. Scarmacca (Super) | Signed inspection reports, all wet areas |  | Not Started
B4 | Firestopping special inspections complete — all rated penetrations | Special Insp. | Special Inspection Agency | A2 | N. Scarmacca (Super) | Signed inspection reports |  | Not Started
B5 | Mechanical / Energy Code compliance special inspection signed off | Special Insp. | Collectif (Mech. Engineer) | A3 | I. Aguire (PM) | Signed TR8 |  | Not Started
B6 | Sprinkler / Fire Alarm special inspection signed off | Special Insp. | Approved Inspector | A2 | I. Aguire (PM) | Signed TR1 for FA / sprinkler |  | Not Started
B7 | FINAL TR1 sign-off letter received from Special Inspection Agency | Special Insp. | Special Inspection Agency | B1,B2,B3,B4,B5,B6 | I. Aguire (PM) | Final TR1 Sign-Off Letter (mandatory TCO prerequisite) |  | Not Started
C. LIFE SAFETY SIGN-OFFS
C1 | Fire alarm 100% device pre-test complete (see Path to Fire Alarm tab) | FDNY | Fire Alarm Sub | A1 | I. Aguire (PM) | Signed 100% device pre-test report |  | Not Started
C2 | FDNY witness / acceptance test passed — Letter of Approval issued | FDNY | FDNY | C1 | I. Aguire (PM) | FDNY Letter of Approval (LOA) |  | Not Started
C3 | Sprinkler hydrostatic test passed — 200 psi / 2 hrs, DOB witnessed | DOB | NYC DOB | A1 | N. Scarmacca (Super) | Signed hydrostatic test record |  | Not Started
C4 | Sprinkler flow test / FDNY field acceptance — waterflow & tamper switches | FDNY | FDNY | C3 | N. Scarmacca (Super) | FDNY field acceptance record |  | Not Started
C5 | Central station alarm transmission verified | FDNY | FDNY / Central Station | C2 | I. Aguire (PM) | Central station verification letter |  | Not Started
D. UTILITY & AGENCY SIGN-OFFS — CMP §19.3 / §20.2
D1 | Electrical rough inspection passed | DOB | DOB Electrical | A1 | I. Aguire (PM) | Rough inspection record |  | Not Started
D2 | Electrical final inspection — Certificate of Electrical Inspection issued | DOB | DOB Electrical | D1 | I. Aguire (PM) | Certificate of Electrical Inspection (or DOB NOW self-cert) |  | Not Started
D3 | Con Edison energisation letter received | Utility | Con Edison | D2 | I. Aguire (PM) | Energisation letter |  | Not Started
D4 | Plumbing rough inspection passed (water / sanitary / vent) | DOB | DOB Plumbing | A1 | N. Scarmacca (Super) | Rough inspection sign-off |  | Not Started
D5 | Gas pressure test passed — 10 psi / 15 min, DOB witnessed | DOB | DOB Plumbing | D4 | N. Scarmacca (Super) | Signed gas pressure test record |  | Not Started
D6 | Gas Activation Notice received | Utility | Con Edison / National Grid | D5 | I. Aguire (PM) | Gas Activation Notice |  | Not Started
D7 | DOB Boiler Unit inspection — after Rheem water heater combustion testing | DOB | DOB Boiler Unit | D6 | I. Aguire (PM) | Boiler inspection sign-off |  | Not Started
D8 | Plumbing final inspection / sign-off | DOB | DOB Plumbing | D5 | N. Scarmacca (Super) | Plumbing final sign-off |  | Not Started
D9 | DEP water meter set | DEP | NYC DEP | A1 | I. Aguire (PM) | Meter set confirmation |  | Not Started
D10 | DEP backflow prevention certification filed | DEP | NYC DEP | D9 | I. Aguire (PM) | Backflow certification |  | Not Started
D11 | DEP final sewer connection approval | DEP | NYC DEP | A1 | I. Aguire (PM) | Sewer connection approval |  | Not Started
E. DOH POOL / SPA — OWNER'S SEPARATE TRADES (CMP §20.3)
E1 | Pool / sauna / cold plunge utility readiness confirmed (electrical, plumbing, trenching) | Internal | Affect Build | D2,D8 | N. Scarmacca (Super) | Utility readiness sign-off |  | Not Started
E2 | Owner's pool vendor testing & commissioning complete | DOH | Owner's Separate Trades | E1 | Owner's Vendor | Vendor commissioning report |  | Not Started
E3 | NYC DOH Pool / Spa final inspection passed | DOH | NYC DOH | E2 | I. Aguire (PM) — coordination only | DOH Pool/Spa approval certificate |  | Not Started
F. COMMISSIONING, QUALITY & CLOSEOUT
F1 | All HVAC equipment startup and functional performance testing complete | Internal | Mechanical Sub / Vendors | A1 | I. Aguire (PM) | Certified startup + FPT reports |  | Not Started
F2 | TAB report issued and accepted | Internal | Approved TAB Firm | F1 | I. Aguire (PM) | TAB report |  | Not Started
F3 | All open NCRs closed (see NCR Log) | Internal | Affect Build | — | I. Aguire (PM) | NCR Log showing zero open items |  | Not Started
F4 | All Tier 3 / Tier 4 DFOW Phase 4 follow-up inspections closed | Internal | Superintendent | — | N. Scarmacca (Super) | Procore inspection records |  | Not Started
F5 | Trade self-punch and Affect Build punch review complete (Phases A & B) | Internal | Affect Build / Trades | F3 | N. Scarmacca (Super) | Punch & RCL Log |  | Not Started
F6 | Owner / Architect punch walk complete (Phase C) | Internal | Owner / Colberg Architecture | F5 | I. Aguire (PM) | Signed punch list |  | Not Started
F7 | O&M Manuals, warranties, as-builts and training certificates compiled | Internal | Affect Build | F1,F2 | I. Aguire (PM) | Certificate and Approvals Binder (digital + hardcopy) |  | Not Started
F8 | Owner systems training delivered and documented | Internal | Subs / Vendors | F7 | I. Aguire (PM) | Training Matrix with attendee sign-in |  | Not Started
G. TCO FILING & ISSUANCE
G1 | Closeout Matrix verified — every authority approval accounted for | Internal | Affect Build | B7,C2,C4,D2,D8,D10,E3 | I. Aguire (PM) | Completed Closeout Matrix |  | Not Started
G2 | TCO application filed via DOB NOW | DOB | NYC DOB | G1 | I. Aguire (PM) | DOB NOW TCO application |  | Not Started
G3 | DOB final building inspection passed | DOB | NYC DOB | G2 | I. Aguire (PM) | Final inspection sign-off |  | Not Started
G4 | TEMPORARY CERTIFICATE OF OCCUPANCY (TCO) ISSUED | DOB | NYC DOB | G3 | I. Aguire (PM) | Issued TCO |  | Not Started
G5 | Final Certificate of Occupancy (CO) issued | DOB | NYC DOB | G4 | I. Aguire (PM) | Issued CO |  | Not Started

## Path to Fire Alarm
SAUNALOUNGE — PATH TO FIRE ALARM SIGN-OFF (FDNY LETTER OF APPROVAL)
The FDNY Letter of Approval (LOA) is a MANDATORY prerequisite for TCO/CO. Per CMP §20.1, FDNY witness testing must be scheduled at least two weeks before the anticipated Substantial Completion date to allow for re-tests.
Substantial Completion Target |  |  | 2026-12-21 | Latest FDNY Test Date (SC − 14 days) |  |  | 2026-12-07 | Steps Complete |  | 0 / 23
Step | Activity / Gate | Responsible Party | Predecessor | Advance Notice Req'd | Target Date | Actual Date | Status | Evidence / Document Required | Notes
FA-01 | Fire alarm shop drawings and device layout submitted to Collectif and Architect for review | Fire Alarm Sub | — | — |  |  | Not Started | Approved shop drawings (Procore submittal)
FA-02 | Fire alarm drawings filed with FDNY / DOB as required; approval obtained | I. Aguire (PM) | FA-01 | 4–6 weeks |  |  | Not Started | FDNY / DOB drawing approval
FA-03 | FACP, RAN and device rough-in complete — Zones A & B | Fire Alarm Sub | FA-02 | — |  |  | Not Started | Pre-cover inspection sign-off
FA-04 | Pre-cover (pre-drywall) inspection of FA rough-in — HOLD POINT | N. Scarmacca (Super) | FA-03 | 48 hrs |  |  | Not Started | Signed pre-cover inspection record (Procore)
FA-05 | Device trim-out complete — initiating, signaling and notification devices installed | Fire Alarm Sub | FA-04 | — |  |  | Not Started | Device installation checklist
FA-06 | Above-ceiling inspection before ACT / grid close-up — HOLD POINT | N. Scarmacca (Super) | FA-05 | 48 hrs |  |  | Not Started | Above-ceiling inspection record
FA-07 | Permanent electrical power available to FACP (energisation sequenced ahead of FA testing) | Electrical Sub | — | — |  |  | Not Started | Con Edison energisation letter / panel energised
FA-08 | Device labelling, zone schedule and as-built riser diagram complete | Fire Alarm Sub | FA-05 | — |  |  | Not Started | As-built riser + zone schedule
FA-09 | 100% pre-test of ALL initiating, signaling and notification devices — HOLD POINT | Fire Alarm Sub | FA-05,FA-07 | 72 hrs |  |  | Not Started | Signed 100% device pre-test report
FA-10 | Interface test — HVAC damper closure on alarm verified | Fire Alarm + Mechanical Subs | FA-09 | 72 hrs |  |  | Not Started | Signed interface test record
FA-11 | Interface test — door hold-open device release on alarm verified | Fire Alarm + Door Hardware Sub | FA-09 | 72 hrs |  |  | Not Started | Signed interface test record
FA-12 | Interface test — sprinkler waterflow and tamper switch supervision to FACP verified | Fire Alarm + Sprinkler Subs | FA-09 | 72 hrs |  |  | Not Started | Signed interface test record
FA-13 | Central station monitoring account active; signal transmission verified | Fire Alarm Sub | FA-09 | — |  |  | Not Started | Central station verification letter
FA-14 | All deficiencies from pre-test corrected and re-tested; zero open NCRs on FA system | I. Aguire (PM) | FA-09,FA-10,FA-11,FA-12 | — |  |  | Not Started | Closed NCR records (see NCR Log)
FA-15 | TR1 special inspection for fire alarm signed by approved inspector | Special Inspection Agency | FA-14 | 1 week |  |  | Not Started | Signed TR1 (fire alarm)
FA-16 | FDNY witness test scheduled — must be on or before latest test date in H4 | I. Aguire (PM) | FA-14 | 2 weeks |  |  | Not Started | FDNY appointment confirmation
FA-17 | Site readiness for FDNY: approved drawings on site, permits posted, inspector sign-in log ready, escort assigned | N. Scarmacca (Super) | FA-16 | — |  |  | Not Started | Readiness checklist + photo record
FA-18 | FDNY WITNESS / ACCEPTANCE TEST — live testing of representative devices | FDNY Inspector | FA-16,FA-17 | — |  |  | Not Started | FDNY field test record
FA-19 | Re-test window (if required) — deficiencies corrected and FDNY re-witness | Fire Alarm Sub / PM | FA-18 | 1 week |  |  | Not Started | Re-test record
FA-20 | FDNY LETTER OF APPROVAL (LOA) ISSUED | FDNY | FA-18 | — |  |  | Not Started | FDNY Letter of Approval — mandatory for TCO
FA-21 | LOA archived in Procore and added to Certificate and Approvals Binder | I. Aguire (PM) | FA-20 | — |  |  | Not Started | Procore record + binder entry
FA-22 | Owner training on fire alarm system delivered and documented | Fire Alarm Sub | FA-20 | — |  |  | Not Started | Training Matrix with attendee sign-in
FA-23 | Fire alarm O&M manual, warranty and as-builts turned over | Fire Alarm Sub | FA-20 | — |  |  | Not Started | O&M manual + warranty letter

## DOH Checklist
SAUNALOUNGE — NYC DEPARTMENT OF HEALTH (DOHMH) COMPLIANCE CHECKLIST ¦ FIRST PASS
FIRST PASS — awareness and coordination checklist, NOT a code compliance certification. Pool, sauna and cold plunge are Owner's Separate Trades under Contract §12.4: furnished, installed, tested and commissioned by the Owner's vendors. Affect Build coordinates access, utility readiness and scheduling, and is NOT responsible for design or performance certification of these systems. EVERY numeric criterion and code citation below must be confirmed by the Owner's DOH consultant and the pool designer against NYS Sanitary Code Subpart 6-1, NYC Health Code Article 165 and Article 81 before it is relied upon.
Total Items | 101 | Verified | 0 | Outstanding | 101 | Affect Build Items | 56 | % Verified | 0%
ID | Item / Requirement to Verify | Responsibility | Affect Build Interface / Exposure | Evidence / Document Required | Status | Verified By | Date | Reference to Confirm | Notes
A. PERMITS, PLAN APPROVAL & ADMINISTRATION
H-01 | Pool / spa construction plans submitted to and approved by DOHMH before construction of the pool shell | Owner / DOH Consultant | AB must not build out enclosing finishes until plan approval is confirmed | Stamped approved DOH plan set |  |  |  | NYC Health Code Art. 165 / NYS Subpart 6-1
H-02 | Confirm whether the facility is classified as a swimming pool, spa, or both — classification drives the applicable requirements | Owner / DOH Consultant | Drives ventilation, drainage and finish requirements in AB scope | Written DOH classification determination |  |  |  | Subpart 6-1 definitions
H-03 | DOH Permit to Operate application filed; permit issued prior to public use | Owner / DOH Consultant | Prerequisite to TCO for pool / sauna areas (CMP §20.3) | Issued DOH Permit to Operate |  |  |  | Art. 165
H-04 | Food Service Establishment permit application for kitchen and bar filed with DOHMH | Owner / DOH Consultant | AB builds out kitchen / bar to DOH-acceptable finishes and equipment rough-in | FSE permit application + issued permit |  |  |  | NYC Health Code Art. 81
H-05 | Food service plan review / pre-permit inspection scheduled with DOHMH | Owner / DOH Consultant | AB coordinates access and completion sequencing | Plan review approval letter |  |  |  | Art. 81
H-06 | Owner's DOH consultant engaged and scope of responsibility documented in writing | Owner / DOH Consultant | Clarifies the boundary between AB scope and Owner's vendors | Consultant agreement / scope letter |  |  |  | Contract §12.4
H-07 | Certified Pool Operator (CPO) or equivalent qualified operator identified before opening | Owner's Separate Trades | None — Owner responsibility; note in turnover package | CPO certificate |  |  |  | Subpart 6-1
H-08 | Safety plan / operation & maintenance plan prepared and submitted as required | Owner's Separate Trades | AB provides equipment O&M data to support the plan | Approved safety plan |  |  |  | Subpart 6-1
H-09 | Confirm whether lifeguard supervision is required for this facility, or 'no lifeguard' operation is permitted | Owner / DOH Consultant | Determines required signage that AB may install | Written DOH determination |  |  |  | Subpart 6-1
B. POOL / SPA STRUCTURE, FINISHES & DECK
H-10 | Pool shell structure and interior finish light in colour, smooth, non-toxic, easily cleaned and non-slip where required | Owner's Separate Trades | AB interface at coping / deck transition only | Product data + DOH approval |  |  |  | Subpart 6-1
H-11 | Water depth markings and 'NO DIVING' markings provided at required locations, contrasting and slip-resistant | Owner's Separate Trades | Confirm tile / marking supply responsibility — AB tile scope excludes coping and waterline band | Photo record + approved layout |  |  |  | Subpart 6-1
H-12 | Depth transition / break in slope clearly marked; safety line and anchors provided where required | Owner's Separate Trades | None | Approved layout |  |  |  | Subpart 6-1
H-13 | Steps, ladders, handrails and recessed treads provided, slip-resistant and securely anchored | Owner's Separate Trades | AB verifies anchorage substrate where anchors land in AB-installed work | Installation certification |  |  |  | Subpart 6-1
H-14 | Deck surface slip-resistant, sloped to drain away from the pool, free of standing water | Shared — AB / Owner's Vendor | AB tile / topping scope at pool deck — slope and slip resistance are AB deliverables | Slope survey + COF test data for tile |  |  |  | Subpart 6-1 / TCNA
H-15 | Minimum unobstructed deck width around the pool perimeter maintained | Shared — AB / Owner's Vendor | AB layout and framing must not encroach — verify against approved DOH plan | Dimensioned as-built plan |  |  |  | Subpart 6-1 — VERIFY DIMENSION
H-16 | Deck drainage provided; deck drains do not discharge to the pool recirculation system | Shared — AB / Owner's Vendor | AB plumbing scope — trench / floor drains and slope | Approved plumbing plan + as-built |  |  |  | Subpart 6-1 / NYC PC
H-17 | Coping, waterline contrast band, step / bench nose tile and plaster finish installed by the pool specialist | Owner's Separate Trades | EXPLICITLY EXCLUDED from AB tile scope per Client Summary — confirm no gap in scope | Scope confirmation letter |  |  |  | Client Summary / Contract §12.4
H-18 | No sharp edges, protrusions or entrapment gaps in the pool, spa or plunge basin | Owner's Separate Trades | AB verifies none created by adjacent AB work | Joint inspection record |  |  |  | Subpart 6-1
H-19 | Barrier / enclosure preventing unsupervised access, with self-closing and self-latching gates where required | Shared — AB / Owner's Vendor | AB may install partitions, doors and hardware forming the barrier | Approved barrier detail + hardware submittal |  |  |  | Subpart 6-1 / Art. 165
C. CIRCULATION, FILTRATION & TURNOVER
H-20 | Recirculation system sized to achieve the required turnover rate for each body of water | Owner's Separate Trades | AB provides electrical and plumbing rough-in and equipment room readiness only | Designer's turnover calculation |  |  |  | Subpart 6-1 — VERIFY TURNOVER RATE
H-21 | Filtration system type, rate and media approved; filter gauges and sight glass provided | Owner's Separate Trades | AB equipment room space, drainage and utilities | Equipment submittal + DOH approval |  |  |  | Subpart 6-1
H-22 | Flow meter installed, accessible and readable on the recirculation line | Owner's Separate Trades | AB piping access and lighting in equipment room | Photo record |  |  |  | Subpart 6-1
H-23 | Hair and lint strainer provided ahead of the pump; accessible for cleaning | Owner's Separate Trades | AB clearance and drainage provision | Equipment submittal |  |  |  | Subpart 6-1
H-24 | Make-up water supplied through an approved air gap or backflow prevention — no direct connection | Shared — AB / Owner's Vendor | AB plumbing scope — make-up water connection and backflow device | DEP backflow certification + DOH acceptance |  |  |  | Subpart 6-1 / NYC PC
H-25 | Pool equipment room floor drainage, sump and pump-out provided; room does not flood | Shared — AB / Owner's Vendor | AB slab, waterproofing, drainage and sump in AB scope | As-built plumbing + flood test record |  |  |  | Subpart 6-1
H-26 | Piping labelled and valve chart posted in the equipment room | Shared — AB / Owner's Vendor | AB labels AB-installed piping; vendor labels vendor piping | Photo record + valve chart |  |  |  | Best practice / Subpart 6-1
H-27 | Gutter / skimmer / overflow system provided per approved design | Owner's Separate Trades | AB interface at deck edge | Approved design |  |  |  | Subpart 6-1
D. DISINFECTION, CHEMISTRY & CHEMICAL STORAGE
H-28 | Automated disinfectant feeder and pH control provided; capable of maintaining required residuals | Owner's Separate Trades | AB power and drainage to chemical controller location | Equipment submittal |  |  |  | Subpart 6-1
H-29 | Automated chemical controller with ORP / pH monitoring installed where required | Owner's Separate Trades | AB power and low-voltage rough-in | Equipment submittal |  |  |  | Subpart 6-1
H-30 | Chemical storage room / area separated, ventilated, with secondary containment and no incompatible storage | Shared — AB / Owner's Vendor | AB constructs and ventilates the chemical storage area — MEP and finishes in AB scope | Approved layout + ventilation calc |  |  |  | Subpart 6-1 / FDNY / NYC MC
H-31 | Eyewash / emergency shower provided at the chemical storage area if required | Shared — AB / Owner's Vendor | AB plumbing scope if required | Approved plumbing plan |  |  |  | OSHA / Subpart 6-1 — VERIFY
H-32 | Test kit(s) appropriate to the disinfectant in use provided on site | Owner's Separate Trades | None | Purchase record |  |  |  | Subpart 6-1
H-33 | Water chemistry, temperature and clarity logs established before opening | Owner's Separate Trades | None | Blank log sheets / digital log |  |  |  | Subpart 6-1
H-34 | Spa / hot tub water temperature limited and temperature display provided | Owner's Separate Trades | AB power to controls | Equipment submittal |  |  |  | Subpart 6-1 — VERIFY MAX TEMP
H-35 | Cold plunge sanitation, filtration and turnover addressed in the approved design | Owner's Separate Trades | AB rough-in only | Approved design |  |  |  | Subpart 6-1
E. ANTI-ENTRAPMENT & SUCTION OUTLETS (VGB)
H-36 | All suction outlets fitted with approved anti-entrapment covers (VGB compliant), within listing date | Owner's Separate Trades | None — but confirm before AB closes any access | Cover certification + installation record |  |  |  | Virginia Graeme Baker Pool & Spa Safety Act
H-37 | Dual drains, unblockable outlet, or approved SVRS / vent system provided as required | Owner's Separate Trades | AB verifies access panels preserved for future service | Approved design + certification |  |  |  | VGB Act / Subpart 6-1
H-38 | Emergency shut-off for pump(s) provided, clearly labelled and accessible from the pool deck | Shared — AB / Owner's Vendor | AB electrical scope — device location, labelling and accessibility | Electrical as-built + photo |  |  |  | Subpart 6-1
H-39 | Main drain visible from the deck / water clarity sufficient to see the bottom | Owner's Separate Trades | None | Clarity test record |  |  |  | Subpart 6-1
F. SAFETY EQUIPMENT, SIGNAGE & SUPERVISION
H-40 | Ring buoy with line and reaching pole / shepherd's hook provided and mounted | Owner's Separate Trades | AB provides blocking / backing in walls where mounted | Photo record |  |  |  | Subpart 6-1
H-41 | First aid kit, spineboard and rescue equipment provided as required | Owner's Separate Trades | AB provides mounting substrate if wall-mounted | Photo record |  |  |  | Subpart 6-1
H-42 | Emergency telephone or communication device accessible from the pool deck | Shared — AB / Owner's Vendor | AB low-voltage rough-in and device location | Photo record + as-built |  |  |  | Subpart 6-1
H-43 | Required signage posted: capacity / bather load, pool rules, no diving, no lifeguard on duty, emergency numbers | Shared — AB / Owner's Vendor | AB signage scope may include fabrication and installation — confirm who supplies DOH-specific signage | Signage schedule + photo record |  |  |  | Subpart 6-1 / Art. 165
H-44 | Bather load / maximum capacity calculated and posted | Owner / DOH Consultant | Affects egress and fixture counts already built by AB — verify no conflict | Capacity calculation |  |  |  | Subpart 6-1
H-45 | Emergency egress from the pool room unobstructed and compliant | Affect Build | AB scope — doors, hardware, egress path, signage | Egress plan + FDNY / DOB sign-off |  |  |  | NYC BC / FDNY
G. SANITARY FACILITIES & BATHHOUSE
H-46 | Toilet, lavatory and shower fixture counts meet the required ratio for the posted bather load | Shared — AB / Owner's Vendor | AB installs all fixtures — a shortfall is an AB rework exposure. Verify counts against DOH bather load NOW | Owner / DOH Consultant calculation + AB fixture schedule |  |  |  | Subpart 6-1 / NYC PC — VERIFY RATIOS
H-47 | Separate facilities provided for each sex as required (men's and women's locker rooms) | Affect Build | AB scope — layout per approved plans | Approved architectural plan |  |  |  | Subpart 6-1 / NYC BC
H-48 | Cleansing showers provided on the route from the locker rooms to the pool deck | Shared — AB / Owner's Vendor | AB plumbing and finish scope — verify route is enforced by the layout | Approved plan + as-built |  |  |  | Subpart 6-1
H-49 | Hot water provided at showers and lavatories, tempered to limit scald risk | Affect Build | AB scope — mixing valves and set points (4x Rheem tankless + ST-120) | Commissioning record with recorded set points |  |  |  | NYC PC — VERIFY MAX TEMP
H-50 | Soap and hand-drying provided at all lavatories | Owner's Separate Trades | AB installs dispensers if in the specialties scope | Photo record |  |  |  | Subpart 6-1 / Art. 81
H-51 | Floors in locker rooms, showers and toilet rooms impervious, slip-resistant, coved and sloped to drain | Affect Build | AB tile, waterproofing and drainage scope — core AB exposure | Slope survey + COF data + flood test |  |  |  | Subpart 6-1 / Art. 81
H-52 | Walls and partitions in wet areas smooth, impervious and easily cleaned to the required height | Affect Build | AB tile, GWB and waterproofing scope | Approved finish schedule + photo record |  |  |  | Subpart 6-1 / Art. 81
H-53 | Toilet partitions and benches non-absorbent and cleanable | Affect Build | AB specialties scope | Product data |  |  |  | Art. 81 / Subpart 6-1
H-54 | Locker room and toilet room ventilation / exhaust provided at the required air change rate | Affect Build | AB mechanical scope — ERV / exhaust fans | TAB report with recorded CFM |  |  |  | NYC MC — VERIFY ACH
H-55 | Drinking water available to bathers | Shared — AB / Owner's Vendor | AB plumbing rough-in if a fountain / filler is provided | As-built plumbing |  |  |  | Subpart 6-1
H-56 | Waste receptacles and cleaning / janitorial provision (mop sink) provided | Affect Build | AB plumbing and specialties scope | As-built plumbing |  |  |  | Art. 81
H. POOL ROOM ENVIRONMENT — VENTILATION, HUMIDITY & LIGHTING
H-57 | Pool room mechanical ventilation and dehumidification sized per code and design (PDU-1 Dectron with dry cooler) | Affect Build | AB mechanical scope — a core AB deliverable and Tier 3 DFOW (D-10) | Certified startup + FPT + TAB report |  |  |  | NYC MC / ASHRAE 62.1 — VERIFY RATE
H-58 | Pool room maintained at negative pressure relative to adjacent spaces to control humidity and odour migration | Affect Build | AB mechanical scope — verify during TAB | TAB report showing pressure relationship |  |  |  | NYC MC / ASHRAE
H-59 | Relative humidity and space temperature control verified and documented | Affect Build | AB mechanical scope | Commissioning record |  |  |  | Design basis / ASHRAE
H-60 | Corrosion-resistant materials used throughout the pool room (ductwork, fasteners, hardware, ceiling grid, light fixtures) | Affect Build | AB scope across multiple trades — a common defect source in pool fitouts | Product data for each material |  |  |  | Design basis / manufacturer
H-61 | Deck and underwater lighting levels meet the required minimum; underwater lights bonded and GFCI protected | Shared — AB / Owner's Vendor | AB electrical scope for deck lighting; vendor for underwater fixtures | Photometric data + electrical test record |  |  |  | Subpart 6-1 / NEC Art. 680 — VERIFY LUX
H-62 | Emergency and egress lighting provided in the pool room and locker rooms | Affect Build | AB electrical scope — also a CGI Public Assembly inspection item | Emergency lighting test record |  |  |  | NYC BC / CGI matrix
H-63 | Equipotential bonding of pool shell, deck reinforcement, ladders, rails and all metal within the required distance | Shared — AB / Owner's Vendor | AB electrical scope for bonding grid — HOLD POINT before deck / slab cover-up | Bonding continuity test record + photos |  |  |  | NEC Art. 680
H-64 | No overhead electrical conductors or unapproved equipment within the prohibited zone above the pool | Affect Build | AB electrical and MEP coordination scope | Coordination drawing + as-built |  |  |  | NEC Art. 680
I. SAUNA, STEAM & COLD PLUNGE
H-65 | Sauna door swings outward and is not fitted with a latch or lock that can trap an occupant | Owner's Separate Trades | AB verifies door hardware if AB supplies the door | Hardware submittal + photo |  |  |  | NYC BC / manufacturer
H-66 | Sauna heater guard, thermostat, high-limit cut-out and timer provided per manufacturer and code | Owner's Separate Trades | AB electrical circuit and disconnect | Equipment submittal + startup record |  |  |  | Manufacturer / NEC
H-67 | Sauna interior finish material approved for the application; no toxic finishes or coatings | Owner's Separate Trades | AB verifies no AB-applied finish enters the sauna envelope | Product data |  |  |  | Manufacturer / Art. 165
H-68 | Emergency call / alarm device provided in sauna and steam rooms if required | Shared — AB / Owner's Vendor | AB low-voltage rough-in | As-built + test record |  |  |  | VERIFY REQUIREMENT
H-69 | Steam room (if provided) sloped ceiling, drainage and vapour-tight construction verified | Shared — AB / Owner's Vendor | AB waterproofing and drainage scope at the interface | Approved detail + flood test |  |  |  | Manufacturer / Subpart 6-1
H-70 | Sauna, steam and plunge room floors slip-resistant and drained | Shared — AB / Owner's Vendor | AB tile, waterproofing and drainage scope | Slope survey + COF data |  |  |  | Subpart 6-1
H-71 | Maximum occupancy and use-duration signage posted for sauna, steam and cold plunge | Owner's Separate Trades | AB signage installation if in scope | Photo record |  |  |  | Subpart 6-1 / manufacturer
H-72 | Cold plunge water temperature control, disinfection and drain-down procedure documented | Owner's Separate Trades | AB rough-in and drainage only | Approved design + O&M |  |  |  | Subpart 6-1
J. WATER SUPPLY, WASTE & CROSS-CONNECTION CONTROL
H-73 | Potable water supply protected from cross-connection throughout the premises | Affect Build | AB plumbing scope — core AB deliverable | DEP backflow certification |  |  |  | NYC PC / DEP
H-74 | Backflow prevention devices installed, tested and certified before occupancy | Affect Build | AB plumbing scope — links to Path to TCO gate D10 | Certified backflow test report |  |  |  | NYC PC / DEP
H-75 | Pool / spa waste and backwash discharged to sanitary sewer via approved means, not to storm | Shared — AB / Owner's Vendor | AB plumbing scope for the connection | Approved plumbing plan + DEP approval |  |  |  | NYC PC / DEP
H-76 | No direct connection between pool piping and the potable water system or the sanitary drainage system | Affect Build | AB plumbing scope | As-built plumbing |  |  |  | NYC PC
H-77 | Water heater / storage temperatures and any Legionella risk management measures addressed | Shared — AB / Owner's Vendor | AB installs the equipment; Owner operates. Confirm whether a water management plan is required | Set-point record + plan if required |  |  |  | ASHRAE 188 — VERIFY APPLICABILITY
K. FOOD SERVICE — KITCHEN & BAR (NYC HEALTH CODE ARTICLE 81)
H-78 | Kitchen and bar floors, walls and ceilings smooth, non-absorbent, light-coloured and easily cleanable | Affect Build | AB finish scope — a core AB deliverable and a common DOH failure point | Approved finish schedule + photo record |  |  |  | Art. 81
H-79 | Coving provided at all floor-to-wall junctions in food preparation and storage areas | Affect Build | AB tile / flooring scope — verify coving detail is in the approved shop drawings | Approved detail + photo record |  |  |  | Art. 81
H-80 | Hand-wash sink(s) provided in the kitchen and bar, dedicated, accessible and with hot and cold water | Affect Build | AB plumbing scope — dedicated handwash is frequently missed at bars | As-built plumbing + photo |  |  |  | Art. 81
H-81 | Three-compartment sink (or approved warewashing) with drainboards provided | Shared — AB / Owner's Vendor | AB plumbing rough-in; equipment by Owner's kitchen vendor | Equipment submittal + as-built |  |  |  | Art. 81
H-82 | Mop / service sink provided and separate from food preparation sinks | Affect Build | AB plumbing scope | As-built plumbing |  |  |  | Art. 81
H-83 | Grease interceptor / trap provided and sized as required; access maintained | Shared — AB / Owner's Vendor | AB plumbing scope — verify sizing with the kitchen consultant | Sizing calculation + as-built |  |  |  | NYC PC / DEP
H-84 | Indirect waste / air gaps provided at all food equipment, ice machines and sinks as required | Affect Build | AB plumbing scope | As-built plumbing |  |  |  | NYC PC / Art. 81
H-85 | Kitchen exhaust hood, make-up air and grease duct installed and balanced (KEF-1 / MUA-1 interlocked) | Affect Build | AB mechanical scope — Tier 3 DFOW (D-10) | TAB report + interlock test record |  |  |  | NYC MC / FDNY / Art. 81
H-86 | Refrigeration and hot-holding equipment capable of holding required temperatures; thermometers provided | Owner's Separate Trades | AB power and drainage rough-in | Equipment submittal + startup temps |  |  |  | Art. 81
H-87 | Adequate lighting levels and shielded / shatter-resistant fixtures in food areas | Affect Build | AB electrical scope | Fixture submittal + photometric data |  |  |  | Art. 81
H-88 | Food-contact and splash surfaces at the bar non-absorbent and sealed (millwork and countertops) | Affect Build | AB millwork scope — sealing at wet edges is an AB exposure | Millwork shop drawings + photo record |  |  |  | Art. 81
H-89 | Vermin exclusion: all penetrations sealed, door sweeps and screens provided, no gaps at walls or slab | Affect Build | AB firestopping, sealing and door hardware scope | Photo record + pre-cover inspection |  |  |  | Art. 81
H-90 | Refuse and recycling storage area constructed to be cleanable and vermin-resistant | Affect Build | AB finish scope | Approved detail + photo record |  |  |  | Art. 81
H-91 | Toilet facilities available for food service staff with hand-wash and self-closing doors | Affect Build | AB scope | Approved plan |  |  |  | Art. 81
L. OPERATIONS, RECORDS & OPERATOR CERTIFICATION
H-92 | Daily operating log established: disinfectant residual, pH, temperature, clarity, bather count | Owner's Separate Trades | None — include in turnover package | Blank / digital log |  |  |  | Subpart 6-1
H-93 | Incident and injury reporting procedure established | Owner's Separate Trades | None | Written procedure |  |  |  | Subpart 6-1
H-94 | Food safety plan / HACCP and food protection certificate holder identified for the kitchen | Owner's Separate Trades | None | Certificate + plan |  |  |  | Art. 81
H-95 | O&M manuals, warranties and training for all AB-installed systems serving DOH-regulated spaces turned over | Affect Build | AB scope — links to Path to TCO gate F7 | Certificate and Approvals Binder |  |  |  | Playbook A10
M. FINAL DOH INSPECTION & OCCUPANCY
H-96 | Pool / spa filled, balanced and operating for the required period before the DOH inspection | Owner's Separate Trades | AB confirms water, power and drainage available in time | Water chemistry log |  |  |  | Subpart 6-1
H-97 | All AB utility readiness complete: electrical energised, plumbing tested, drainage operational, ventilation balanced | Affect Build | AB scope — links to Path to TCO gate E1 | Utility readiness sign-off |  |  |  | CMP §20.3
H-98 | DOH Pool / Spa final inspection scheduled with minimum 2 weeks notice and AB escort assigned | Shared — AB / Owner's Vendor | AB coordinates access and escorts the inspector; inspector signs the site log | Inspector Sign-In entry + inspection record |  |  |  | CMP §20.3 / Trainual SOP
H-99 | DOH Pool / Spa approval certificate issued and archived | Owner / DOH Consultant | Mandatory prerequisite to TCO — links to Path to TCO gate E3 | DOH approval certificate |  |  |  | CMP §20.4
H-100 | DOH food service pre-permit inspection passed and permit issued for kitchen / bar | Owner / DOH Consultant | AB completes all Article 81 finish and equipment items beforehand | Issued FSE permit |  |  |  | Art. 81
H-101 | All DOH certificates added to the Certificate and Approvals Binder for Owner turnover | Affect Build | AB scope | Binder index |  |  |  | CMP §20.4

## Statutory Inspections
SAUNALOUNGE — STATUTORY INSPECTION & AGENCY APPROVAL LOG (DOB · FDNY · DOH · DEP · UTILITIES)
Superintendent coordinates all inspections 48–72 hours in advance and records results immediately upon completion. Every inspector must sign the physical site log (see Inspector Sign-In tab). Final signed reports are compiled into the closeout package for TCO/CO issuance. (CMP §12.4, §12.6)
Total | 24 | Passed | 0 | Failed / Re-inspect | 0 | Outstanding | 24 | Certificates Received |  | 0
ID | Inspection / Approval | Agency | Discipline | DOB NOW / Filing Ref | Requested Date | Scheduled Date | Inspector Name | Result | Re-Insp. Date | Certificate / Document Received | Date Closed | Status | Linked TCO Gate | Notes
S-01 | PW1 / PW2 permit issuance | NYC DOB | Permit | [8 empty] | Open | A1
S-02 | Electrical rough inspection | DOB Electrical | Electrical | [8 empty] | Open | D1
S-03 | Electrical final inspection / Certificate of Electrical Inspection | DOB Electrical | Electrical | [8 empty] | Open | D2
S-04 | Con Edison energisation / energisation letter | Con Edison | Electrical | [8 empty] | Open | D3
S-05 | Plumbing rough inspection — water / sanitary / vent | DOB Plumbing | Plumbing | [8 empty] | Open | D4
S-06 | Gas pressure test witness — 10 psi / 15 min | DOB Plumbing | Gas | [8 empty] | Open | D5
S-07 | Gas Activation Notice | Con Edison / National Grid | Gas | [8 empty] | Open | D6
S-08 | DOB Boiler Unit inspection — Rheem water heaters | DOB Boiler Unit | Plumbing | [8 empty] | Open | D7
S-09 | Plumbing final inspection / sign-off | DOB Plumbing | Plumbing | [8 empty] | Open | D8
S-10 | DEP water meter set | NYC DEP | Water | [8 empty] | Open | D9
S-11 | DEP backflow prevention device certification | NYC DEP | Water | [8 empty] | Open | D10
S-12 | DEP final sewer connection approval | NYC DEP | Sewer | [8 empty] | Open | D11
S-13 | Sprinkler hydrostatic test witness — 200 psi / 2 hrs | NYC DOB | Fire Protection | [8 empty] | Open | C3
S-14 | Sprinkler flow test / FDNY field acceptance — waterflow & tamper | FDNY | Fire Protection | [8 empty] | Open | C4
S-15 | FDNY fire alarm witness / acceptance test | FDNY | Fire Alarm | [8 empty] | Open | C2
S-16 | FDNY Letter of Approval (LOA) issuance | FDNY | Fire Alarm | [8 empty] | Open | C2
S-17 | Central station alarm transmission verification | FDNY / Central Station | Fire Alarm | [8 empty] | Open | C5
S-18 | NYC DOH Pool / Spa final inspection | NYC DOH | Pool / Spa | [8 empty] | Open | E3
S-19 | DOB final building inspection | NYC DOB | Building | [8 empty] | Open | G3
S-20 | TCO issuance | NYC DOB | Building | [8 empty] | Open | G4
S-21 | Final Certificate of Occupancy issuance | NYC DOB | Building | [8 empty] | Open | G5
S-22 | DOB Chapter 33 site safety inspection (unannounced) | NYC DOB | Site Safety | [8 empty] | Open | —
S-23 | FDNY site inspection — hot work / standpipe / egress (unannounced) | FDNY | Site Safety | [8 empty] | Open | —
S-24 | OSHA inspection (unannounced) | OSHA | Site Safety | [8 empty] | Open | —

## Special Inspections
SAUNALOUNGE — SPECIAL INSPECTIONS LOG (NYC BC CHAPTER 17 · TR1 / TR2 / TR3 / TR8)
Special Inspections for Tier 3 / Tier 4 DFOWs are MANDATORY HOLD POINTS — work may not advance until the report is received and uploaded to Procore. Notify the agency min. 48 hrs in advance. Every inspector must sign the physical site log. Final TR1 sign-off letter is a mandatory TCO prerequisite. (Playbook A6 / CMP §12.6)
Total Events | 36 | Passed | 0 | Failed | 0 | Reports Outstanding |  | 36 | Sign-In Verified |  | 0
ID | Special Inspection Type | Category / TR Ref | Agency / Inspector Firm | Frequency / Trigger | DFOW Ref | Location / Zone | Notice Given | Inspection Date | Inspector Name | Sign-In Log Verified | Result | Report Received | Procore Ref | NCR Raised | Status | Notes
SI-01 | Concrete placement — pool equipment room slab | TR2 / TR3 | Licensed Testing Laboratory | Each pour | D-07 | Pool equipment room | [8 empty] | Open
SI-02 | Concrete pre-pour rebar, embeds & formwork verification | TR3 | CodeGreen Inspection (CGI) | Before every pour | D-07 | Pool equipment room | [8 empty] | Open | CGI: allow min. 2-3 days to schedule site visit
SI-03 | Concrete compressive strength testing (cylinder breaks) | TR2 | Licensed Testing Laboratory | 1 set per 50 CY min. | D-07 | Pool equipment room | [8 empty] | Open
SI-04 | Excavation / support of excavation verification | TR4 / TR5 | CodeGreen Inspection (CGI) | Before and during excavation | D-08 | Pool equipment room | [8 empty] | Open | CGI Structural Stability — 2 budgeted visits
SI-05 | Subgrade / soil bearing verification | TR4 | CodeGreen Inspection (CGI) | Before slab placement | D-08 | Pool equipment room | [8 empty] | Open | CGI Structural Stability — 2 budgeted visits
SI-06 | Waterproofing — wet-area interface (locker rooms, showers, pool deck) | TR12/13-adjacent | Independent Inspector | Prior to backfill / cover-up | D-01 | Zones A & B wet areas | [8 empty] | Open
SI-07 | Waterproofing interface at Owner's pool shell / sauna / cold plunge | TR12/13-adjacent | Independent Inspector | Prior to cover-up, each interface | D-02 | Pool room (Zone B) | [8 empty] | Open
SI-08 | Firestopping of rated penetrations | Ch.17 Firestop | CodeGreen Inspection (CGI) | Each rated penetration, before cover | D-15 | Whole premises | [8 empty] | Open | CGI Fire Stopping — inspector must witness installation
SI-09 | Mechanical systems / energy code compliance | TR8 | CodeGreen Inspection (CGI) | At system completion | D-10, D-11 | Roof / Zones A & B | [8 empty] | Open | CGI Energy Code (EC) progress inspection — 3 budgeted visits
SI-10 | Duct leakage / pressure testing witness | TR8 | CodeGreen Inspection (CGI) / Collectif | Each system before close-up | D-11 | Zones A & B | [8 empty] | Open | CGI MH Systems — 3 budgeted visits; approved HVAC balance report + equipment submittals required prior to sign-off
SI-11 | Mechanical ventilation / exhaust verification | TR8 | CodeGreen Inspection (CGI) / Collectif | At system completion | D-10 | Zones A & B | [8 empty] | Open | CGI MH Systems — prior to installation of ceilings or other finishes
SI-12 | Energy code — insulation, air sealing & lighting controls | TR8 | CodeGreen Inspection (CGI) | Progressive, before cover-up | D-24 | Whole premises | [8 empty] | Open | CGI Energy Code (EC) progress inspection
SI-13 | Sprinkler system — hydrostatic and flow testing | TR1 / FDNY | CodeGreen Inspection (CGI) | Final acceptance | D-04 | Whole premises | [8 empty] | Open | CGI SP Systems hydro test — 1 budgeted visit; prior to connection of new system to building main
SI-14 | Fire alarm system — 100% device acceptance test | TR1 / FDNY | Approved Inspector | Final acceptance | D-03 | Whole premises | [8 empty] | Open
SI-15 | Fire-resistance rated construction / penetrations verification | Ch.17 | CodeGreen Inspection (CGI) | Progressive, before cover-up | D-15, D-20 | Whole premises | [8 empty] | Open | CGI Fire Stopping / Fire Proofing
SI-16 | Structural steel / miscellaneous metals connections (if in scope) | TR1 | CodeGreen Inspection (CGI) | Each connection type | D-18 | Zones A & B | [8 empty] | Open
SI-17 | Post-installed anchors in concrete / masonry | TR1 | CodeGreen Inspection (CGI) | Per approved frequency | D-07 | Zones A & B | [8 empty] | Open | CGI Post Installed Anchors — 1 budgeted visit; installers must be NYC DOB certified; inspector witnesses ALL phases
SI-18 | DOH Pool / Spa inspection (Owner's Separate Trades) | DOH | NYC DOH Inspector | Prior to occupancy of pool / sauna areas | — | Pool room (Zone B) | [8 empty] | Open
SI-19 | FINAL TR1 SIGN-OFF LETTER — Special Inspection Agency | TR1 Final | CodeGreen Inspection (CGI) | Once, all inspections closed | All | Whole premises | [8 empty] | Open | CGI Directive 14 final sign-off prerequisite
SI-20 | FINAL TR8 SIGN-OFF — Mechanical / Energy | TR8 Final | CodeGreen Inspection (CGI) / Collectif | Once, all inspections closed | All mech. | Whole premises | [8 empty] | Open | CGI Energy Code final
SI-21 | Preliminary inspection — prior to any work being performed | Ch.17 Preliminary | CodeGreen Inspection (CGI) | Once, before any work commences | All | Whole premises | [8 empty] | Open | CGI budgeted: 1 visit. Must occur PRIOR TO any work being performed
SI-22 | Fireproofing — spray-applied / intumescent (if in scope) | Ch.17 Fireproofing | CodeGreen Inspection (CGI) | Progressive during application | D-15 | Whole premises | [8 empty] | Open | CGI Fire Proofing inspection type
SI-23 | Public assembly — emergency lighting & exit signs | Ch.17 / Public Assembly | CodeGreen Inspection (CGI) | Once, after installation | D-24 | Whole premises | [8 empty] | Open | CGI budgeted: 0 visits — confirm scope. Space must be blacked out or inspect after dark
SI-24 | Directive 14 — final inspection / Owner's Statement of Construction | Directive 14 (OT Construct) | CodeGreen Inspection (CGI) | Once, at completion of all work | All | Whole premises | [8 empty] | Open | CGI budgeted: 1 visit. AFTER completion of all approved work AND sign-off of all other controlled inspections
CODEGREEN INSPECTION (CGI) — BUDGETED SPECIAL INSPECTION PROGRAMME ¦ Matrix ref. 2026-0401 ¦ Client Rep: Jeffrey Aser, Teal Development Partners (914.319.7493, jeff@tealdevelopment.com) ¦ ALLOW MINIMUM 2–3 DAYS TO SCHEDULE A SITE VISIT
# | CGI Inspection Type | Budgeted Visits | Trigger — inspect AFTER… | Constraint — must occur PRIOR TO… | Visits Used | Visits Remaining | Notes / Conditions
1 | Preliminary | 1 | — | Any work being performed on site |  | 1 | First CGI visit — schedule before mobilisation
2 | Structural Stability | 2 | Approval of shop drawings / demo procedures; AND after excavation and/or exposure of any existing soils, foundation or structure to remain, and installation of all shoring / supports | Removal of any structural floor slab, foundation component, structural element, and/or transfer of any permanent load to a modified structure or component |  | 2 | Covers pool equipment room excavation and any structural modification
3 | Post Installed Anchors | 1 | Approval of anchors, installation procedures and embedment depth | Commencement of installation |  | 1 | Inspector must witness ALL phases of installation. Installers must be certified per NYC DOB requirements
4 | Fire Stopping |  | Installation of firestop systems at rated penetrations | Cover-up of any rated penetration |  |  | Budgeted visit count not legible on the CGI matrix — confirm with CodeGreen
5 | Fire Proofing |  | Application of spray-applied / intumescent fireproofing | Enclosure or cover-up |  |  | Budgeted visit count not legible on the CGI matrix — confirm with CodeGreen; confirm whether in scope for this fitout
6 | SP Systems (Sprinkler — hydro test) | 1 | Completing installation of all piping, hangers and sprinkler heads (concurrent with hydro test) | Connection of the new system to the building main |  | 1 | Coordinate with the 200 psi / 2 hr hydrostatic test (ITP T-08)
7 | MH Systems (Mechanical, Heating, Chimneys) | 3 | Installation of equipment, ductwork, louvers, dampers, controls and piping | Installation of ceilings or other finishes |  | 3 | Approved HVAC balance report AND equipment submittals required prior to inspection sign-off
8 | Energy Code (EC) — Progress Inspection | 3 | Installation of heating and/or mechanical equipment, lighting, exit signs, windows and other components whose performance is mandated by the Energy Code | Installation of ceilings or other finishes that will hinder inspection |  | 3 | TR8 pathway — coordinate with Collectif
9 | Public Assembly — Emergency Lighting | 0 | Emergency lights and exit signs have been installed | — |  | 0 | Space must be blacked out, or inspection scheduled after dark. 0 visits budgeted — confirm scope
10 | Directive 14 — Final (Owner's Statement of Construction) | 1 | Completion of ALL construction work shown on the approved drawings AND sign-off of all other controlled inspections | — |  | 1 | Final CGI visit. Prerequisite to TCO — links to Path to TCO gate B7 / G1
| TOTAL BUDGETED VISITS | 12 |  |  | 0 | 12

## Inspector Sign-In
SAUNALOUNGE — INSPECTOR SITE SIGN-IN LOG (MANDATORY)
NON-NEGOTIABLE: Every inspector — DOB, FDNY, DOH, DEP, Special Inspection Agency, Testing Laboratory, OSHA — must sign in physically on arrival BEFORE conducting any inspection. Required for DOB audit defence and TCO. Maintain a bound ledger at the foreman's desk / site entry; this tab is the digital mirror. Superintendent or designated staff must escort at all times.
Date | Time In | Time Out | Inspector Printed Name | Company / Firm | Agency | Inspection Type | Area / Zone Inspected | Escorted By (Affect) | Result | Report / Log Ref | Signature Obtained | Uploaded to Procore | Notes

## Commissioning
SAUNALOUNGE — COMMISSIONING, START-UP & TURNOVER MATRIX
No system is energised, started or commissioned without documented readiness: Phase 4 inspections closed, PFCs signed, controls point-to-point tested, ZERO open Tier 3/4 deficiencies, and all documentation available. Sequence: pre-functional / vendor startup → functional performance testing → documentation → re-test if required → sign-off. (Playbook A8 / CMP §9)
Total Systems | 38 | FPT Complete | 0 | Training Complete |  | 0 | O&M Received |  | 0 | Turnover Readiness |  | 0%
Tag | System / Equipment | Manufacturer / Model | Scope By | Location | DFOW Ref | Pre-Functional Checklist | Vendor Startup Report | Point-to-Point / Controls | Functional Perf. Test | TAB Required | Training Delivered | O&M Manual | Warranty Letter | As-Built / Record Dwg | Status | Notes
RT-1 | Rooftop heat pump — 15 ton with 30 kW electric heat | Thermotek | Affect Build | Roof | D-10 |  |  |  |  | Yes |  |  |  |  | Not Started
PDU-1 | Pool room air conditioning unit with outdoor dry cooler | Dectron | Affect Build | Pool room (Zone B) / Roof | D-10 |  |  |  |  | Yes |  |  |  |  | Not Started
ERV-1 | Energy recovery ventilator | Valent / Fantech | Affect Build | Roof / Zone A | D-10 |  |  |  |  | Yes |  |  |  |  | Not Started
ERV-2 | Energy recovery ventilator | Valent / Fantech | Affect Build | Roof / Zone B | D-10 |  |  |  |  | Yes |  |  |  |  | Not Started
AC-1 | Split system air conditioning unit | Mitsubishi | Affect Build | Zone A | D-10 |  |  |  |  | Yes |  |  |  |  | Not Started
AC-2 | Split system air conditioning unit | Mitsubishi | Affect Build | Zone A | D-10 |  |  |  |  | Yes |  |  |  |  | Not Started
AC-3 | Split system air conditioning unit | Mitsubishi | Affect Build | Zone A | D-10 |  |  |  |  | Yes |  |  |  |  | Not Started
AC-4 | Split system air conditioning unit | Mitsubishi | Affect Build | Zone B | D-10 |  |  |  |  | Yes |  |  |  |  | Not Started
AC-5 | Split system air conditioning unit | Mitsubishi | Affect Build | Zone B | D-10 |  |  |  |  | Yes |  |  |  |  | Not Started
MUA-1 | Make-up air unit | Greenheck | Affect Build | Roof | D-10 |  |  |  |  | Yes |  |  |  |  | Not Started
KEF-1 | Kitchen exhaust fan | Greenheck | Affect Build | Roof / Kitchen | D-10 |  |  |  |  | Yes |  |  |  |  | Not Started
EF / SF | Exhaust and supply fans (general) | Greenheck | Affect Build | Roof / Zones A & B | D-10 |  |  |  |  | Yes |  |  |  |  | Not Started
ACCU-1 | Air-cooled condensing unit — reconnect | Existing | Affect Build | Roof | D-12 |  |  |  |  | No |  |  |  |  | Not Started
ACCU-2 | Air-cooled condensing unit — reconnect | Existing | Affect Build | Roof | D-12 |  |  |  |  | No |  |  |  |  | Not Started
ACCU-3 | Air-cooled condensing unit — new | TBC | Affect Build | Roof | D-12 |  |  |  |  | No |  |  |  |  | Not Started
DUCT-A | Ductwork Zone A — pressure / leakage test | — | Affect Build | Zone A | D-11 |  |  |  |  | Yes |  |  |  |  | Not Started
DUCT-B | Ductwork Zone B (pool room) — pressure / leakage test | — | Affect Build | Zone B | D-11 |  |  |  |  | Yes |  |  |  |  | Not Started
SWBD-1 | Main switchboard | TBC | Affect Build | Electrical room | D-05 |  |  |  |  | No |  |  |  |  | Not Started
MP-1 | Main distribution panel | TBC | Affect Build | Electrical room | D-05 |  |  |  |  | No |  |  |  |  | Not Started
KP-1 | Kitchen panel | TBC | Affect Build | Kitchen | D-05 |  |  |  |  | No |  |  |  |  | Not Started
LP-1 | Lighting panel | TBC | Affect Build | Electrical room | D-05 |  |  |  |  | No |  |  |  |  | Not Started
RP-1 | Receptacle panel | TBC | Affect Build | Electrical room | D-05 |  |  |  |  | No |  |  |  |  | Not Started
LTG-CTL | Lighting controls / dimming system (Exhibit G allowance) | TBC | Affect Build | Whole premises | D-24 |  |  |  |  | No |  |  |  |  | Not Started
AV / LV | Low-voltage, data and AV systems | TBC | Affect Build | Whole premises | D-23 |  |  |  |  | No |  |  |  |  | Not Started
FA-SYS | Fire alarm system — FACP, RAN and all devices (100% device test) | TBC | Affect Build | Whole premises | D-03 |  |  |  |  | No |  |  |  |  | Not Started
FS-SYS | Fire sprinkler system — 87 new heads, main and branch | TBC | Affect Build | Whole premises | D-04 |  |  |  |  | No |  |  |  |  | Not Started
WH-1 | Tankless gas water heater | Rheem | Affect Build | Mechanical room | D-09 |  |  |  |  | No |  |  |  |  | Not Started
WH-2 | Tankless gas water heater | Rheem | Affect Build | Mechanical room | D-09 |  |  |  |  | No |  |  |  |  | Not Started
WH-3 | Tankless gas water heater | Rheem | Affect Build | Mechanical room | D-09 |  |  |  |  | No |  |  |  |  | Not Started
WH-4 | Tankless gas water heater | Rheem | Affect Build | Mechanical room | D-09 |  |  |  |  | No |  |  |  |  | Not Started
ST-120 | Hot water storage tank | Rheem ST-120 | Affect Build | Mechanical room | D-09 |  |  |  |  | No |  |  |  |  | Not Started
GAS-SVC | Elevated-pressure gas service connection and activation | Con Ed / National Grid | Affect Build | Kitchen / mechanical | D-06 |  |  |  |  | No |  |  |  |  | Not Started
BFP-1 | Backflow prevention device | TBC | Affect Build | Water entry | D-13 |  |  |  |  | No |  |  |  |  | Not Started
EXTR-1 | Water extractor (voltage substitution per RFI) | Suitemate | Affect Build | Locker rooms | D-13 |  |  |  |  | No |  |  |  |  | Not Started
POOL | Pool shell, filtration and circulation system | Owner's Vendor | Owner's Separate Trades (§12.4) | Pool room (Zone B) | — |  |  |  |  | No |  |  |  |  | Not Started
SAUNA | Sauna interior assemblies, heater and controls | Owner's Vendor | Owner's Separate Trades (§12.4) | Sauna (Zone B) | — |  |  |  |  | No |  |  |  |  | Not Started
PLUNGE | Cold plunge basin and chiller | Owner's Vendor | Owner's Separate Trades (§12.4) | Pool room (Zone B) | — |  |  |  |  | No |  |  |  |  | Not Started
KITCH | Kitchen equipment package | Owner's Vendor | Owner's Separate Trades (§12.4) | Kitchen | — |  |  |  |  | No |  |  |  |  | Not Started

## Submittals & Mockups
SAUNALOUNGE — SUBMITTAL, SAMPLE & MOCK-UP REGISTER
No fabrication or procurement begins prior to written approval. Review cross-checks specification compliance, code compliance and coordination with adjacent systems. Mock-ups authorise release of full production — no production begins until the mock-up is formally signed off. Typical A/E review 10–14 calendar days. (CMP §8.5 / Playbook A4, A5.5)
Total | 39 | Approved | 0 | Rejected / Revise |  | 0 | Outstanding | 39 | Long-Lead Items |  | 8
ID | Spec / CSI Section | Submittal Description | Type | DFOW Ref | Responsible Sub / Vendor | Long Lead | Required On Site | Date Submitted | Reviewer | Date Returned | Review Status | Released for Fab. | Mock-Up Sign-Off Date | Status | Notes
SUB-001 | 23 00 00 | HVAC equipment package — RT-1, PDU-1, ERV-1/2, AC-1 to AC-5 (Exhibit C early release) | Product Data | D-10 | Mechanical Sub | Yes |  |  | Collectif |  |  |  |  | Open
SUB-002 | 23 31 00 | Ductwork shop drawings — Zones A & B | Shop Drawing | D-11 | Mechanical Sub | No |  |  | Collectif |  |  |  |  | Open
SUB-003 | 23 23 00 | Refrigerant piping layout and specialties | Shop Drawing | D-12 | Mechanical Sub | No |  |  | Collectif |  |  |  |  | Open
SUB-004 | 26 20 00 | Switchgear, panelboards and distribution — SWBD-1, MP-1, KP-1, LP-1, RP-1 | Product Data | D-05 | Electrical Sub | Yes |  |  | Collectif |  |  |  |  | Open
SUB-005 | 26 09 00 | Lighting controls / dimming system (Exhibit G allowance) | Shop Drawing | D-24 | Electrical Sub | No |  |  | Collectif |  |  |  |  | Open
SUB-006 | 26 50 00 | Lighting fixture package | Product Data | D-24 | Electrical Sub | Yes |  |  | Colberg Architecture |  |  |  |  | Open
SUB-007 | 28 31 00 | Fire alarm shop drawings, device layout and riser diagram | Shop Drawing | D-03 | Fire Alarm Sub | No |  |  | Collectif |  |  |  |  | Open
SUB-008 | 21 13 00 | Fire sprinkler hydraulic calculations and shop drawings (87 heads) | Shop Drawing | D-04 | Sprinkler Sub | No |  |  | Collectif |  |  |  |  | Open
SUB-009 | 22 33 00 | Domestic hot water — 4x Rheem tankless + ST-120 storage tank | Product Data | D-09 | Plumbing Sub | Yes |  |  | Collectif |  |  |  |  | Open
SUB-010 | 22 40 00 | Plumbing fixtures and trim (incl. Kohler finish substitution per RFI) | Product Data | D-13 | Plumbing Sub | No |  |  | Colberg Architecture |  |  |  |  | Open
SUB-011 | 22 11 19 | Backflow prevention device and DEP certification package | Product Data | D-13 | Plumbing Sub | No |  |  | Collectif |  |  |  |  | Open
SUB-012 | — | Suitemate water extractor — voltage substitution (per RFI) | Product Data | D-13 | Plumbing Sub | No |  |  | Collectif |  |  |  |  | Open
SUB-013 | 07 10 00 | Wet-area waterproofing system — membrane, primers, detailing | Product Data | D-01 | Waterproofing Sub | No |  |  | Colberg Architecture |  |  |  |  | Open
SUB-014 | 07 10 00 | Waterproofing interface details at Owner's pool / sauna assemblies | Shop Drawing | D-02 | Waterproofing Sub | No |  |  | Colberg / Owner's Vendor |  |  |  |  | Open
SUB-015 | 07 84 00 | Firestopping — UL listed systems schedule | Product Data | D-15 | Firestopping Sub | No |  |  | Collectif |  |  |  |  | Open
SUB-016 | 07 50 00 | Roofing / flashing details at RTU-1 curbs and penetrations | Shop Drawing | D-17 | Roofing Sub | No |  |  | Colberg Architecture |  |  |  |  | Open
SUB-017 | 03 30 00 | Concrete mix designs — pool equipment room slab | Product Data | D-07 | Concrete Sub | No |  |  | Structural Engineer |  |  |  |  | Open
SUB-018 | 03 20 00 | Reinforcing steel shop drawings and bar lists | Shop Drawing | D-07 | Concrete Sub | No |  |  | Structural Engineer |  |  |  |  | Open
SUB-019 | 31 20 00 | Support of excavation drawings (PE-stamped) | Shop Drawing | D-08 | Excavation Sub | No |  |  | Structural Engineer |  |  |  |  | Open
SUB-020 | 09 22 00 | Metal stud framing — barrel vault and soffit shop drawings | Shop Drawing | D-18 | Drywall Sub | No |  |  | Colberg Architecture |  |  |  |  | Open
SUB-021 | 04 23 00 | Glass block wall system | Product Data | D-19 | Masonry Sub | No |  |  | Colberg Architecture |  |  |  |  | Open
SUB-022 | 09 30 00 | Tile & stone package — TL-1, TL-2, TL-3, setting materials, grout | Sample | D-14 | Tile Sub | Yes |  |  | Colberg Architecture |  |  |  |  | Open
SUB-023 | 09 64 00 | Wood flooring — pool / lounge accent | Sample | D-29 | Flooring Sub | No |  |  | Colberg Architecture |  |  |  |  | Open
SUB-024 | 09 65 00 | Resilient flooring and base | Sample | D-27 | Flooring Sub | No |  |  | Colberg Architecture |  |  |  |  | Open
SUB-025 | 09 51 00 | ACT / acoustic ceiling panels and grid | Product Data | D-25 | Ceiling Sub | No |  |  | Colberg Architecture |  |  |  |  | Open
SUB-026 | 09 90 00 | Paint and wall covering schedule | Sample | D-28 | Painting Sub | No |  |  | Colberg Architecture |  |  |  |  | Open
SUB-027 | 06 40 00 | Millwork shop drawings — lockers, reception desk, entry gates, self-check-in kiosk | Shop Drawing | D-16 | Millwork Sub | Yes |  |  | Colberg Architecture |  |  |  |  | Open
SUB-028 | 06 40 00 | Millwork shop drawings — bar, coat check, kitchen casework | Shop Drawing | D-16 | Millwork Sub | Yes |  |  | Colberg Architecture |  |  |  |  | Open
SUB-029 | 08 11 00 | Door, frame and hardware schedule (incl. hold-open devices) | Shop Drawing | D-21 | Door Sub | Yes |  |  | Colberg Architecture |  |  |  |  | Open
SUB-030 | 10 21 00 | Toilet partitions, bath accessories and lockers | Product Data | D-30 | Specialties Sub | No |  |  | Colberg Architecture |  |  |  |  | Open
SUB-031 | 10 14 00 | Signage and wayfinding package | Shop Drawing | D-31 | Signage Sub | No |  |  | Colberg Architecture |  |  |  |  | Open
MU-01 | 09 30 00 | MOCK-UP — Tile & stone: pool deck / shower assembly incl. waterproofing transition | Mock-Up | D-14, D-01 | Tile + Waterproofing Subs | No |  |  | Q-Team + Architect + Owner |  |  |  |  | Open
MU-02 | 09 29 00 | MOCK-UP — GWB Level 5 skim finish panel | Mock-Up | D-20 | Drywall Sub | No |  |  | Q-Team + Architect |  |  |  |  | Open
MU-03 | 06 40 00 | MOCK-UP — Locker unit and reception desk first article | Mock-Up | D-16 | Millwork Sub | No |  |  | Q-Team + Architect + Owner |  |  |  |  | Open
MU-04 | 03 35 00 | MOCK-UP — Polished / sealed concrete floor sample at BOH | Mock-Up | D-27 | Concrete Finisher | No |  |  | Q-Team + Architect |  |  |  |  | Open
MU-05 | 09 90 00 | MOCK-UP — Paint and wall covering sample area | Mock-Up | D-28 | Painting Sub | No |  |  | Q-Team + Architect |  |  |  |  | Open
MU-06 | 04 23 00 | MOCK-UP — Glass block wall panel | Mock-Up | D-19 | Masonry Sub | No |  |  | Q-Team + Architect |  |  |  |  | Open
MU-07 | 07 84 00 | MOCK-UP — Firestopping typical penetration (UL system) | Mock-Up | D-15 | Firestopping Sub | No |  |  | Q-Team + SIA |  |  |  |  | Open
MU-08 | 09 64 00 | MOCK-UP — Wood flooring accent panel at pool / lounge | Mock-Up | D-29 | Flooring Sub | No |  |  | Q-Team + Architect |  |  |  |  | Open

## Checklist
SAUNALOUNGE — DFOW / INSPECTION TYPE MATRIX | INSPECTION
| Control Sample | First Delivery | Benchmark | Mock-up | Checklist | Handover | Q-Team Sign-off | Quality Control
| ⬜ | ⬜ | ⬜ |  |  |  | ⬜ | ⬜
| ⬜ | ⬜ | ⬜ |  |  |  | ⬜ | ⬜
| ⬜ | ⬜ | ⬜ |  |  |  | ⬜ | ⬜
| ⬜ | ⬜ | ⬜ |  |  |  | ⬜ | ⬜
| ⬜ | ⬜ | ⬜ |  |  |  | ⬜ | ⬜
| ⬜ | ⬜ | ⬜ |  |  |  | ⬜ | ⬜
| ⬜ | ⬜ | ⬜ |  |  |  | ⬜ | ⬜
| ⬜ | ⬜ | ⬜ |  |  |  | ⬜ | ⬜
| ⬜ | ⬜ | ⬜ |  |  |  | ⬜ | ⬜
| ⬜ | ⬜ | ⬜ |  |  |  | ⬜ | ⬜
| ⬜ | ⬜ | ⬜ |  |  |  | ⬜ | ⬜
| ⬜ | ⬜ | ⬜ |  |  |  | ⬜ | ⬜
| ⬜ | ⬜ | ⬜ |  |  |  | ⬜ | ⬜
| ⬜ | ⬜ | ⬜ |  |  |  | ⬜ | ⬜
Waterproofing
Waterproofing interface with pool
Concrete
Self-Levelling
Tile Material
TL 1
TL 2
TL 3
Tile Install
TL 1
TL 2
TL 3
Drywall L 5
Polished Concrete
Countertops
Doors & Hardware
Blocking
Painting
Millwork
Bathroom Stalls
Roofing Flood Test
Lighting Controls
Brick
Mortar
Railings
Firestopping
Pre-Ceiling Close-up
Pre-Wall Close-up
Pre Concrete Pour

## Sample Size
Inspection Sample Size Chart with Guidance
How to Use This Inspection Sample Size Chart This chart provides guidance on how many units (or how much area/length) to inspect when full inspection isn’t practical.
Step 1: Determine Quantity Type - Count, SF, or LF based on the scope.
Step 2: Find the Range - Match your total installed quantity with the closest range.
Step 3: Apply the Sample Size - Use recommended units or percentages spread across locations.
Step 4: Scale Up if Issues Found - Double sample or inspect 100% if defects found.
Note on Standards
This chart aligns with the principles of ANSI/ASQ Z1.4 and ISO 2859-1 but is simplified for construction QA/QC use.
Quantity Type | Quantity Range | Square Footage Equivalent | Recommended Sample Size | Typical Use Case
Count | 1–8 items | N/A | 100% (all) | Fixtures, doors, fire extinguishers
Count | 9–25 items | N/A | 5 | Appliances, windows, casework units
Count | 26–50 items | N/A | 8 | Electrical devices, hardware
Count | 51–90 items | N/A | 13 | Backing, anchors, devices
Count | 91–150 items | N/A | 20 | Light fixtures, support hangers
Count | 151–280 items | N/A | 32 | Fasteners, brackets
Count | 281–500 items | N/A | 50 | Small MEP accessories
Square Footage | 0–200 SF | 0–200 SF | 100% | Patching, small rooms
Square Footage | 201–500 SF | 201–500 SF | 10–20% or 1 sample / 50 SF | Waterproofing, flooring mockups
Square Footage | 501–1,000 SF | 501–1,000 SF | 10% or 1 sample / 75 SF | Tiling, GWB, concrete flatwork
Square Footage | 1,001–5,000 SF | 1,001–5,000 SF | 5–10% | Traffic coatings, roofing membrane
Square Footage | 5,001–20,000 SF | 5,001–20,000 SF | 2–5% | Vapor barrier, slab surface inspection
Linear Footage | 0–100 LF | N/A | 100% | Trim, cove bases, waterproofing at base
Linear Footage | 101–250 LF | N/A | 10% or 1 sample per 20 LF | Pipe insulation, railings
Linear Footage | 251–1,000 LF | N/A | 5–10% | Framing, caulking, edge protection
Linear Footage | 1,001–5,000 LF | N/A | 3–5% | MEP runs, control joints
Linear Footage | 5,001+ LF | N/A | 2–3% | Exterior caulking, firestopping

## FlowChart
Type | Requirement | Expectation | Tool / Format | Sign-Off | Stored Where
First Delivery Inspection | Inspect first shipment of materials for type, spec compliance, and damage | Materials match approved submittals before use | Procore Inspection Checklist | Superintendent + Subcontractor | Procore > Inspections
Material Handover | Documenting Affect purchased materials to installer. Ex. Door hardware, bathroom accessories, Kitchen cabinets. | Log trade partner acceptance/rejection of materials. Scan in signed ticked with Affect countersign. | Procore Documents Tool | Superintendent + Subcontractor | Procore Documents Tool / Sharepoint
Benchmark Inspection | First installation of any repeated system (e.g. walls, ceilings, facade, MEP) | Reviewed by Q-Team to establish project quality standard | Procore Inspection + Benchmark Form | Q-Team incl. Architect/Owner | Procore > Benchmarks / PDF binder
Mock-Up Review | Construct mock-ups for key finishes or assemblies (tile, millwork, facade) | Review for workmanship and aesthetic prior to repeated work | In-field physical sample + photo log | Architect / Client Rep | Onsite + Procore Photo Documentation
Non-Conformance Report (NCR) | Documented deviation from plans/specs or unacceptable workmanship | Issued immediately, tracked to closure | Procore Observations Tool | Superintendent / PM | Procore > Observations
Control Samples | Keep one sample of each approved material onsite | Used as reference for quality and installation checks | Stored physically in labeled plastic box | — | Site Office Sample Bin
Punchlist Walks | Final completion walkthrough for trade and general scopes | Deficiency list generated in detail and issued per trade | Procore Punchlist Tool | PM / Architect / Client | Procore > Punchlists
Monthly QA Review | Review completed vs. missed benchmarks | Ensure compliance, identify areas of risk or inaction | Internal Project Schedule / QA Log | PM / Superintendent | Project Folder / QA Dashboard

## NCR Log (hidden)
SAUNALOUNGE — OBSERVATION / NON-CONFORMANCE REPORT (NCR) LOG
ALL QUALITY ISSUES LIVE IN PROCORE. Seven-step process: Identify (same day) → Issue (24 hrs) → Tag (same day) → Root Cause (48 hrs) → Corrective Action (48 hrs) → Verification → Closure. A missed First Work Review, a rejected material left on site, or work past a Hold Point without sign-off are all NCR events. NCR items must be closed before the next progress billing is approved. (Playbook A7 / CMP §8.7)
Total Raised | 0 | Open | 0 | Closed | 0 | Overdue | 0 | Avg Days to Close |  | —
NCR # | Date Raised | Type | Raised By | DFOW Ref | Trade / Subcontractor | Location / Zone | Description of Non-Conformance | Spec / Submittal Ref | Photos in Procore | Physically Tagged | Root Cause Received | Contributing Cause Category | Corrective Action Plan | Resolution | Target Close Date | Verified By | Date Closed | Days Open | Status | Notes
Formulas:
Days Open = IF([Date Raised]="","",IF([Date Closed]<>"",[Date Closed]-[Date Raised],TODAY()-[Date Raised]))

## Punch & RCL Log
SAUNALOUNGE — PUNCH LIST & ROLLING COMPLETION LIST (RCL)
Punch is NOT Quality Control — punch confirms readiness. ZERO PUNCH is the objective. Four-phase process: A Trade Self-Punch (mandatory gate) → B Affect Build Review → C Owner / A/E Walk (SC gate) → D Back Punch (final close). Response within 2 working days; standard correction within 5 working days; life-safety / occupancy-impacting items within 48 hours. No retainage release for any trade until their punch items are fully closed and Superintendent-verified. (Playbook A9 / D-K)
Total Items | 0 | Open | 0 | Closed | 0 | Life Safety Items Open |  | 0 | Aged > 7 Days |  | 0 | % Closed | 0%
Item # | Date Raised | Phase | Area / Room | Trade / Subcontractor | Description | Classification | Life Safety / Occupancy Impact | Assigned To | Response Due | Target Correction | Date Corrected | Verified By | Days Open | Date Closed | Status | Notes
Formulas:
Response Due = IF([Date Raised]="","",WORKDAY([Date Raised],2))
Target Correction = IF([Date Raised]="","",IF([Life Safety / Occupancy Impact]="Yes",[Date Raised]+2,WORKDAY([Date Raised],5)))
Days Open = IF([Date Raised]="","",IF([Date Closed]<>"",[Date Closed]-[Date Raised],TODAY()-[Date Raised]))

## Excavation
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: EXCAVATION
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 31 20 00 |  | D-08 | Tier 3
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Pool equipment room
CHECKLIST STATUS |  | Items | 19 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Soil information report is on job and reviewed
2 | Note elevation of water table
3 | Monuments and stakes are located
4 | Utilities to remain are located, staked and protected
5 | Verify utility companies have been notified
6 | Shoring and underpinning is provided if required
7 | Spillage of soil on streets removed for public safety
8 | Provide public safety: fences, barricades, etc.
9 | Excavating does not cause unusual rutting
10 | Drainage is provided continuously
11 | Are well points required?
12 | Drainage ditches are maintained
13 | Testing, inspection and compaction as required
14 | Compaction is performed in lifts required
15 | Building layout established
16 | Elevations are established
17 | Observe setbacks and batter boards
18 | Footing drains installed as specified
19 | Waterproofing protected during backfilling
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Concrete Formwork
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: CONCRETE FORMWORK
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 03 10 00 |  | D-07 | Tier 3
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Pool equipment room
CHECKLIST STATUS |  | Items | 25 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Location, dimension and grades as required
2 | Re-used formwork reconditioned and treated
3 | Formwork treatment compatible with other materials
4 | Provide mortar-tight condition, free from offsets
5 | Formwork provides structural sections
6 | End forms deepened as required for pipes, conduits, etc.
7 | Forms provide for depressed slab, cut-outs, curbs
8 | Sleeves for piping and conduits are as required
9 | Provisions made for anchors, hangers and bucks
10 | Verify number and location of cleanouts and ports
11 | Cleanouts provided at ends and low points of forms
12 | Ports are provided in high forms
13 | Forms in alignment, especially at top of walls
14 | Keys are provided in construction joints
15 | Forms provide for door and window openings
16 | Provide cross bracing in formed openings
17 | Observe types of form spacers, ties and bracing
18 | Check spacing of ties to be set to a pattern
19 | Check alignment of chamfer and nail strips and chases
20 | Observe elevation and anchoring of trench ducts
21 | Provisions made during pour for sawed joints
22 | Expansion, construction and contraction joints as required
23 | Filler securely fastened in expansion joints
24 | Forms secured against movement during placing
25 | Verify removal of temporary spreaders
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Conc Reinforcement
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: CONC REINFORCEMENT
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 03 20 00 |  | D-07 | Tier 3
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Pool equipment room
CHECKLIST STATUS |  | Items | 26 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Grade of steel delivered as required
2 | Spacing coordinated to suit masonry units
3 | Required clearance of steel from forms provided
4 | Length of splices and staggering of splices as required
5 | Bends within radii and tolerance are uniformly made
6 | Additional bars at intersections, openings and corners
7 | Bars cleaned of material that might reduce bond
8 | Dowels for marginal bars at wall ends and openings
9 | Beam bars spliced near supports for bottom steel
10 | Splice near midspan for top steel
11 | No bent bars and tension members installed
12 | Vertical bars at wall ends set inside horizontal bars
13 | Extra turns at top and bottom of spiral columns
14 | Bars tied and supported to prevent displacement
15 | Spacers, tie wires and chairs as required
16 | Conduits are separated 3 conduit diameters minimum
17 | No conduit or pipe placed below rebar material
18 | No liquid-carrying pipes are embedded
19 | No contact of bars is made with dissimilar metals
20 | Bars not near surfaces that allow rusting
21 | Rebars are welded only with approval
22 | Adequate clearance provided for deposit of concrete
23 | Review drawings for anchors, piping, sleeves, boxes
24 | Resolve conflicts between embedded items and reinforcement
25 | Special coating as required
26 | Cantilever reinforcement — proper placement
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## CIP Concrete
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: CIP CONCRETE
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 03 30 00 |  | D-07 | Tier 3
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Pool equipment room
CHECKLIST STATUS |  | Items | 28 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Approval of forms and rebar prior to pour
2 | Requirements for tests, mix design, ingredients confirmed
3 | Test lab notified prior to pour
4 | Testing is arranged at plant and site
5 | Foundations are free of frost and water
6 | Previously placed concrete properly prepared for new
7 | Vibrators and stand-by vibrators are available
8 | Temporary form openings, tremies and chutes provided
9 | Pockets are vented to prevent air entrapment
10 | Sub-base and capillary fills compacted
11 | Arrange for specified curing and sawed joints
12 | Arrange for cold weather protection if needed
13 | Cylinders, measuring equipment and slump cone at site
14 | Modified grout provided for rebar congestion
15 | Layers are kept horizontal in required lifts
16 | Placement rate maintained to avoid cold joints
17 | Bolts and loose items properly located and installed
18 | Date and location of pours is recorded
19 | Elevations, alignment and supports checked during pour
20 | Time for concrete to settle before placing concrete above
21 | Obtain approval concerning watering at site
22 | Cylinders are cast and stored properly
23 | Verify finishes: smooth, exposed aggregate, colored
24 | Screeds are provided as required
25 | No troweling while bleed water is on surface
26 | Curing compounds compatible with finishes
27 | Finishing method provides tolerance indicated
28 | Slopes are provided to properly drain
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Precast Concrete
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: PRECAST CONCRETE
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 03 40 00 |  | D-07 | Tier 3
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Not in current scope — retained for scope changes
CHECKLIST STATUS |  | Items | 21 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Required samples for finish, anchors, reinforcement
2 | Test procedure established for fabricator
3 | Special items and conditions understood
4 | Mock-up provided and approved
5 | Structural support items located and installed
6 | Check anchors and fasteners for type of metal and size
7 | Material protected by shields during welding
8 | Joint and panel alignment within tolerance
9 | Back-up caulk, cement and materials are non-staining
10 | Joint caulking and sealing as required
11 | Flexible gaskets for joints are properly sealed
12 | Caulking checked for type, color and method
13 | Coping bolts and dowel holes are grouted
14 | Observe location of expansion or control joints
15 | Built-in flashing formed and located
16 | Weep holes are provided
17 | Remove lead buttons or wood wedges
18 | Check water-repellent materials and methods
19 | Protection provided for projecting sills and work
20 | Cleaning proceeds from top downward
21 | Protection provided during cleaning
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Unit Masonry
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: UNIT MASONRY
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 04 20 00 |  | D-19 | Tier 2
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Zone A — glass block / CMU
CHECKLIST STATUS |  | Items | 31 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Approved shop drawings are on site
2 | Approved samples are on site or evidenced
3 | Mortar mix and ingredients approved
4 | Sample panels provided and approved
5 | Materials stored off ground and covered
6 | Concrete masonry units are not wet
7 | Reinforcement: type, size, splicing and spacing
8 | Do not allow excessive bending of rebar
9 | Pipes, sleeves and boxes located
10 | No shovel measures for job-mixed grout
11 | Climatic and temperature conditions are suitable
12 | Adequate lighting provided for good workmanship
13 | Story pole is used for coursing
14 | Joint size, type and tooling method as required
15 | Bonding is as required
16 | Observe full head and bed joints
17 | Joints tooled to provide dense surface
18 | Wythes or cavities kept free of excess droppings
19 | Check anchors and ties for material, size and set
20 | Bucks and anchors secured, plumb and level
21 | Provisions for flashings, cut-outs and later items
22 | Provisions for parging if required
23 | Expansion and control joints are located
24 | Weeps are provided if required
25 | Structural members have suitable attachments
26 | Debris is removed periodically, not piled
27 | Protect work from freezing at least 48 hours
28 | Clean off splatters from finish surfaces
29 | Observe bond beam filling
30 | Hollow metal frames are filled solid
31 | Backfilling after proper curing and support
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Metal Deck
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: METAL DECK
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 05 31 00 |  | D-18 | Tier 2
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Not in current scope — retained for scope changes
CHECKLIST STATUS |  | Items | 30 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Material approved type, shapes, gauge and size
2 | Approved samples are on job if required
3 | Review approved decking layout submissions
4 | Material is properly stored on site and protected
5 | All accessory items are furnished and approved type
6 | Welding inspection by testing laboratory if required
7 | Welders are certified if required
8 | Sequence of fastening is performed
9 | Closures at edges are provided as required
10 | Decking in contact with beams; proper tack welds
11 | Observe tabs and hangers for equipment and ceilings
12 | Coordination with sheet metal, roofing, insulation, electrical
13 | Decking is continuous over supports if required
14 | Welded connections and spacings are as required
15 | Observe panel-to-panel seams for tack weld
16 | Check seam welding for burn-outs
17 | Reinforcement at columns and penetrations as required
18 | Reinforcement at major concentrated loads as required
19 | Type, spacing and alignment of seam connections as required
20 | Electric cell units are aligned
21 | No rough edges to damage wire pulled through cells
22 | Butt ends taped to keep concrete fill out
23 | No concentrated loads on decks during construction
24 | Verify if shoring is required for concrete topping
25 | Deck is free of loose dirt and debris before topping
26 | On roof decking, deslag welds and paint with zinc
27 | Verify if UL labels are required
28 | Roof ventilation provisions are met
29 | Touch up exposed and cut galvanized metal
30 | Record all damaged panels
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Slab on Grade
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: SLAB ON GRADE
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 03 30 00 |  | D-07 | Tier 3
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Pool equipment room / BOH
CHECKLIST STATUS |  | Items | 19 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Mix design approved
2 | Curing compounds (if any) compatible with finishes
3 | Finishing method provides for tolerances specified
4 | Forms and reinforcement approved prior to placement
5 | Underground / under-slab utilities in place
6 | Elevations, alignment and support checked during pour
7 | Sub-grade fine graded and compacted
8 | Required box-outs, openings and haunches in place
9 | Properly sloped to drains
10 | Testing arranged and testing agency notified
11 | Obtain water at site
12 | Arrange for cold weather protection if needed
13 | Bolts and loose items properly located and installed
14 | Mesh size and gauge as required; flat sheets; proper lap
15 | Area of placement free of frost and water
16 | No troweling while bleed water is on surface
17 | Verify finishes
18 | Date and location of pour(s) recorded
19 | Wet spray or moist curing adequately performed
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Slab on Deck
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: SLAB ON DECK
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 03 30 00 |  | D-07 | Tier 3
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Not in current scope — retained for scope changes
CHECKLIST STATUS |  | Items | 13 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Pour stops and reinforcement approved prior to placement
2 | Decking, studs and flashing complete
3 | Under-slab utilities in place
4 | Required box-outs, openings and haunches in place
5 | Bolts and loose items properly located and installed
6 | Mesh size and gauge as required; flat sheets; proper lap
7 | Arrange for cold weather protection if needed
8 | Area of placement free of frost and water
9 | Decks blown off
10 | Elevations, alignment and support checked during pour
11 | Properly sloped to drains
12 | Curing compound applied
13 | Date and location of pour(s) recorded
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Waterproofing
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: WATERPROOFING
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 07 10 00 |  | D-01 / D-02 | Tier 4
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Zones A & B — all wet areas, pool interface
CHECKLIST STATUS |  | Items | 27 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Approved submittal, product data and warranty terms on site
2 | Manufacturer's certified applicator confirmed and documented
3 | Substrate clean, dry, sound and within moisture tolerance
4 | Moisture testing of substrate performed and recorded
5 | Ambient and substrate temperature within manufacturer's limits
6 | Cracks, honeycomb and voids repaired prior to application
7 | Cove and fillet detailing at all floor-to-wall transitions
8 | Corners, changes of plane and control joints reinforced
9 | Primer applied at specified rate and cure time observed
10 | Membrane thickness / wet mil thickness verified and logged
11 | Reinforcing fabric embedded at all detail locations
12 | All penetrations (drains, sleeves, anchors) sealed and detailed
13 | Floor drain clamping ring correctly set and sealed
14 | Curb, threshold and door transition detailing complete
15 | Sauna, cold plunge and pool interface terminations continuous
16 | Interface with Owner's Separate Trades assemblies witnessed jointly
17 | Vertical membrane turn-up height per detail verified
18 | Overlaps and seams at required minimum lap width
19 | Flood test performed: minimum 24 hrs at 2 in. head
20 | Flood test results recorded with photographs and signed off
21 | No loss of head and no evidence of leakage below
22 | Repairs after failed flood test re-tested and re-signed
23 | Protection board / screed installed without membrane damage
24 | Membrane protected from following trades until covered
25 | Pre-cover HOLD POINT signed off before tile or topping
26 | Special inspection report received and uploaded to Procore
27 | Warranty documentation issued and filed for closeout
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Drywall Framing
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: DRYWALL FRAMING
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 09 22 00 |  | D-18 | Tier 2
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Zones A & B
CHECKLIST STATUS |  | Items | 28 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Material is stored in dry location
2 | Material does not overload floor system
3 | Materials galvanized where exposed to damp conditions
4 | Studs are doubled up at jambs
5 | Reinforced and heavy gauge studs as required
6 | Studs allow for movement: shrinkage, slab deflection
7 | Studs securely anchored to walls and columns
8 | Studs securely anchored to floor plates
9 | Soundproofing provided at floors and walls as required
10 | Locations, layout and plumbness are verified
11 | Channel stiffeners are provided as required
12 | Special fastening and connection accuracy observed
13 | Anchor blocking, plates and other equipment provided
14 | Cut studs for openings are properly framed
15 | Observe size and gauge of runner and furring channels
16 | Hangers are saddle-tied, bolted or clipped as required
17 | Tie wire for channels to runners properly tied
18 | Elevation and layout of furring is understood
19 | Provide a true plane surface, plumb or level
20 | Provide long single lengths
21 | Control joint installation method is understood
22 | Provide for adjoining surfaces of different materials
23 | Sealing provided for sound or thermal isolation
24 | Wood studs are in alignment
25 | Out-of-line wood members are corrected
26 | Spacing and construction are as specified if wood
27 | Blocking, bracing and nailers to attach wallboard
28 | Wood is dry to avoid nail pops due to shrinkage
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Drywall Board
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: DRYWALL BOARD
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 09 29 00 |  | D-20 | Tier 2
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Zones A & B
CHECKLIST STATUS |  | Items | 28 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Type, thickness, length and edges are as required
2 | Type of fastener, length and spacing as required
3 | Installation complies with manufacturer's requirements
4 | Special type used for damp locations if required
5 | Special lengths are provided if required
6 | Verify if horizontal or critical application is required
7 | Wallboard is installed with staggered application
8 | Internal and external metal corners as required
9 | Number of coatings required is provided
10 | Sanding between coats is performed
11 | Feathering is out 12 in. to 16 in.
12 | Provide air circulation with adequate dry heat
13 | Fire-rated: recesses over 16 in. boxed in
14 | Penetrations tight and sealed as required by codes
15 | Cut-outs and outlet boxes correct to avoid patching
16 | Require sawing; no scoring or knock-outs
17 | Wallboard is held up from floor 3/8 in. minimum
18 | Vertical joints are aligned with door jambs
19 | Damaged sheets are not used and are removed
20 | Observe minimum piecing or jointing
21 | Nailing from center out; paper surfaces not broken
22 | Non-metallic cable, plastic or copper is not damaged
23 | Check for bubbles and dimples
24 | Curing time is adequate
25 | Clean-up at intervals is performed
26 | Excessive debris does not accumulate
27 | Prevent tracking to other areas
28 | Refer to US Gypsum Handbook for good practices
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Firestopping
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: FIRESTOPPING
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 07 84 00 |  | D-15 | Tier 3
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Whole premises — all rated penetrations
CHECKLIST STATUS |  | Items | 22 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Approved UL listed systems schedule on site for all conditions
2 | Correct UL system selected for each penetration type
3 | Installer trained / certified per manufacturer requirements
4 | Annular space within listed system tolerances
5 | Penetrating item type and size matches listed system
6 | Backing / packing material correct type and compression
7 | Depth of sealant verified against listed system
8 | Sealant / mortar / wrap product within shelf life
9 | Substrate clean and free of dust, oil and moisture
10 | Sleeves installed and correctly sized where required
11 | Cast-in devices installed to correct depth and orientation
12 | Head-of-wall joints firestopped to correct detail
13 | Rated wall abandoned penetrations sealed
14 | Membrane penetrations (boxes) spaced and protected per code
15 | Fire dampers installed with correct sleeve and retaining angles
16 | Rated ceiling penetrations protected as required
17 | Labelling applied adjacent to each firestop location
18 | Photographic record captured before cover-up
19 | Mock-up of typical condition reviewed and approved
20 | Special inspection performed before cover-up (HOLD POINT)
21 | Deficiencies logged as NCR and re-inspected after correction
22 | Firestop log maintained and uploaded to Procore
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Metal Frames
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: METAL FRAMES
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 08 11 13 |  | D-21 | Tier 2
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Whole premises
CHECKLIST STATUS |  | Items | 17 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Fabrication and construction of frames as required
2 | Smooth joints welded if required
3 | Gauge, size, straightness and features as required
4 | Frames are pre-braced if required
5 | Extra reinforcement at head, corners and hardware
6 | Adequate provisions made to receive hardware
7 | Proper type and number of anchors are provided
8 | Verify adequate anchorage made during installation
9 | Sound deadening treatment is provided if required
10 | Fire-rated frames have labels and proper identification
11 | Light/sound-proof and lead-lined frames as required
12 | Provide features such as silencer holes if required
13 | Frame is grouted during installation if required
14 | Frame is caulked if required
15 | Frames are installed straight, level and plumb
16 | Frames adequately braced where built in
17 | Priming or factory finish is provided
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Metal Doors
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: METAL DOORS
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 08 11 13 |  | D-21 | Tier 2
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Whole premises
CHECKLIST STATUS |  | Items | 25 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Doors are as approved — size, type and design
2 | Check panel, lights, louvers and features
3 | Check defects: dents, buckles and warps
4 | Fabrication, construction and workmanship
5 | Smooth edges and joints, finish and straightness
6 | Additional reinforcement provided for hardware
7 | Observe backing plates during drilling operations
8 | Observe that closure channels are provided
9 | Provisions to receive hardware are adequate
10 | Observe type of factory-installed hardware
11 | Backset is matched to finish hardware
12 | Stile edges and astragals required for pairs of doors
13 | Fire-rated doors have labels and proper identification
14 | Wire glass is provided
15 | Fusible-link holders provided at louvers
16 | Observe installation and verify proper clearance
17 | Doors are hung straight, level and plumb
18 | Door functions smoothly and easily
19 | Hardware is properly adjusted
20 | Observe glazing operation
21 | Factory prime is retouched
22 | Surfaces are adequate to receive applied finish
23 | Report doors that cannot be properly cleaned
24 | Protection provided to avoid marring
25 | Bumper buttons installed
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Doors & Hardware
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: DOORS & HARDWARE
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 08 71 00 |  | D-21 | Tier 2
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Whole premises
CHECKLIST STATUS |  | Items | 22 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Approved door, frame and hardware schedule on site
2 | Hardware delivered, inventoried and stored securely
3 | Hardware matches approved schedule and keying plan
4 | Fire-rated assemblies carry correct labels (door, frame, hardware)
5 | Frame anchorage type and count per approved detail
6 | Frames set plumb, level and square within tolerance
7 | Rough openings sized correctly and blocking present
8 | Undercut and floor clearance per detail and code
9 | Hinge quantity and size correct for door weight
10 | Closers adjusted for opening force per ADA requirements
11 | Panic and exit devices operate freely and latch positively
12 | Door hold-open devices interfaced to fire alarm and tested
13 | Smoke and acoustic seals continuous and correctly installed
14 | Thresholds set in sealant and level
15 | Lever heights and operation compliant with ADA
16 | Wet-area doors and hardware corrosion-resistant per spec
17 | Glazing type, labels and setting blocks per spec
18 | Signage and room numbering coordinated
19 | Doors operate smoothly with no binding or dragging
20 | Finishes free from damage; touch-up complete
21 | Keying delivered, tested and turned over to Owner
22 | Hardware O&M and warranty documentation submitted
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Tile & Stone
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: TILE & STONE
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 09 30 00 |  | D-14 | Tier 3
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Zones A & B — pool, lockers, showers, lounge, bar, kitchen
CHECKLIST STATUS |  | Items | 24 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Approved samples and mock-up signed off before production
2 | Tile / stone type, size, finish and lot verified against approval
3 | Material inspected for damage, warpage and shade variation
4 | Substrate flatness within specified tolerance for tile size
5 | Waterproofing membrane complete, flood tested and signed off
6 | Movement joints located per TCNA / EJ171 and detail
7 | Setting materials and grout per approved submittal
8 | Mortar coverage verified by periodic tile pull-up test
9 | Back-buttering performed where required for large format
10 | Layout established from control lines; dry layout reviewed
11 | Cuts sized to avoid slivers; symmetry maintained
12 | Slope to drains verified before and after setting
13 | Trim, edge profiles and transitions per detail
14 | Grout joint width consistent and per spec
15 | Grout colour and type correct; cured before cleaning
16 | Sealant (not grout) at all changes of plane
17 | Anti-slip / coefficient of friction requirement met in wet areas
18 | Coping, waterline band and bench nose tile by pool specialist — interface verified
19 | Lippage within specified tolerance
20 | Sounding of set tile for hollow spots performed
21 | Penetrations, escutcheons and fixtures neatly cut and sealed
22 | Surfaces protected from following trades
23 | Sealer / impregnator applied per manufacturer if specified
24 | Final clean complete with no residue or haze
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Resilient Flooring
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: RESILIENT FLOORING
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 09 65 00 |  | D-27 | Tier 2
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
BOH / Zone A
CHECKLIST STATUS |  | Items | 28 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Certificates and affidavits have been received
2 | Samples are on site, if required
3 | Type, pattern and color of material is as approved
4 | Primer, adhesive or cement is as required
5 | Base complies with approvals
6 | Containers labeled, sealed and unopened
7 | Boxes inspected for damage in transit
8 | Floor material is stored at proper temperature
9 | Pre-formed corners and end stops are provided
10 | Proper sequence with other trades
11 | All areas are cleaned before installation
12 | On slabs, surfaces are primed if required
13 | On slabs, moisture tests are performed if required
14 | Area temperature maintained during and after installation
15 | Observe pattern matching in sheet material
16 | Direction of tile is as specified
17 | Cement applied at proper rate and proper tackiness
18 | Observe joints and seams are tight and level
19 | Minimum length of pieces is observed
20 | Verify provisions for thresholds and joinings
21 | Verify level joining at electrical cover plates
22 | Excess adhesive removed after installation
23 | Scuffed, broken or discolored tile is replaced
24 | Rolled material unrolled 24 hrs before installation
25 | Sheet flooring is rolled starting from center
26 | Temporary protective cover is provided if required
27 | Prepare subfloor for receiving flooring
28 | Verify compatibility with floor hardener
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## ACT Ceilings
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: ACT CEILINGS
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 09 51 00 |  | D-25 | Tier 2
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Zones A & B
CHECKLIST STATUS |  | Items | 20 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Above-ceiling MEP coordination inspection signed off (HOLD POINT)
2 | All above-ceiling work tested, inspected and labelled
3 | Ceiling height and datum verified against reflected ceiling plan
4 | Grid layout matches RCP; borders symmetrical
5 | Suspension wires plumb, spacing per spec, 4 twists minimum
6 | Independent support for light fixtures and diffusers
7 | Seismic / lateral bracing per detail where required
8 | Perimeter angle level within tolerance
9 | Grid level within 1/8 in. in 10 ft
10 | Panel type, edge detail and finish per approved submittal
11 | Panels handled with clean gloves; no soiling or damage
12 | Access panels located per coordination and accessible
13 | Sprinkler head escutcheons centred in tile
14 | Diffusers, grilles and devices centred and square
15 | Cut tiles clean and neatly fitted
16 | Barrel vault and soffit transitions per detail
17 | Wet-area ceiling panels moisture-resistant type per spec
18 | Fire-rated ceiling assemblies per listed detail
19 | Punch and damage repair complete before turnover
20 | Attic stock quantity delivered to Owner
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Millwork & Casework
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: MILLWORK & CASEWORK
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 06 40 00 |  | D-16 | Tier 3
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Zones A & B — lockers, reception, bar, coat check, kitchen
CHECKLIST STATUS |  | Items | 24 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Approved shop drawings and finish samples on site
2 | Field dimensions verified before fabrication (VIF)
3 | First article / shop visit review completed and signed off
4 | Material species, grade and core per approved submittal
5 | AWI / manufacturer quality grade confirmed
6 | Delivered units inspected for damage, warp and finish defects
7 | Moisture content of wood within specified range
8 | Site conditions acclimatised before installation
9 | Blocking and in-wall backing verified before close-in
10 | Anchorage type and count per detail; secure to structure
11 | Units installed plumb, level and square
12 | Scribes, fillers and reveals consistent and tight
13 | Countertop seams tight, supported and sealed
14 | Wet-area substrates and edges sealed against moisture
15 | Sink and appliance cut-outs sized and sealed
16 | Hardware type, quantity and operation per spec
17 | Drawers and doors aligned with consistent gaps
18 | Soft-close and locking hardware functions correctly
19 | Lockers, reception desk, gates and kiosk fit and function verified
20 | Bar and coat check millwork coordination with MEP verified
21 | ADA clearances and heights verified
22 | Finish touch-up complete; no visible damage
23 | Protection installed until turnover
24 | O&M, warranty and attic stock provided
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Painting
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: PAINTING
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 09 90 00 |  | D-28 | Tier 1
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Whole premises
CHECKLIST STATUS |  | Items | 19 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Approved colour schedule and samples on site
2 | Mock-up / sample area approved before production
3 | Product, sheen and system match approved submittal
4 | Substrate clean, dry, sound and within moisture limits
5 | Surface preparation per manufacturer requirements
6 | Ambient and surface temperature and humidity within limits
7 | Ventilation adequate during application and cure
8 | Adjacent surfaces and finishes masked and protected
9 | Primer type correct for each substrate
10 | Number of coats per spec applied and recorded
11 | Dry film thickness / coverage rate verified
12 | Wet-area and high-humidity coatings correct type
13 | Cut lines sharp and straight at transitions
14 | No holidays, runs, sags, lap marks or roller stipple
15 | Wall covering pattern match and seams verified
16 | Hardware, plates and devices removed and reinstalled
17 | Mechanical and electrical items painted or masked per spec
18 | Touch-up and final coat after punch complete
19 | Attic stock and colour records provided to Owner
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Electrical
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: ELECTRICAL
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 26 00 00 |  | D-05 | Tier 4
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Whole premises — Zone A & Zone B (pool room)
CHECKLIST STATUS |  | Items | 25 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Approved shop drawings, panel schedules and submittals on site
2 | Equipment matches approved submittal (SWBD-1, MP-1, KP-1, LP-1, RP-1)
3 | Working clearances at panels per NEC and code
4 | Conduit routing coordinated; no conflicts with other trades
5 | Conduit supports and spacing per code
6 | Box type, size and fill compliant; wet-location boxes where required
7 | Pre-cover inspection of rough-in signed off (HOLD POINT)
8 | Wire type, size and colour code per spec and NEC
9 | Grounding and bonding continuity tested and recorded
10 | Insulation resistance (megger) test complete before energisation
11 | Breaker sizes and settings match panel schedule
12 | Panel and circuit labelling complete and accurate
13 | Arc flash / equipment labelling applied
14 | Zone A and Zone B (pool room) wiring methods per code for damp locations
15 | GFCI protection provided in all required wet locations
16 | Pool / spa equipment bonding verified per NEC Article 680
17 | Roof equipment disconnects installed and labelled
18 | Low-voltage and AV rough-in separated per spec
19 | Lighting fixtures installed, aimed and lamped per RCP
20 | Lighting controls and dimming scenes tested and accepted
21 | Fire alarm interface circuits verified
22 | DOB electrical rough inspection passed
23 | DOB electrical final inspection / Certificate of Electrical Inspection obtained
24 | Con Edison energisation letter received
25 | As-built panel schedules and O&M turned over
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Plumbing
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: PLUMBING
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 22 00 00 |  | D-06 / D-13 | Tier 4
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Whole premises
CHECKLIST STATUS |  | Items | 26 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Approved submittals for fixtures, valves and equipment on site
2 | Material type and rating per spec (CW, HW, waste, vent, gas)
3 | Pipe supports, hangers and spacing per code
4 | Sleeves and firestopping at all rated penetrations
5 | Insulation type and thickness per spec; vapour barrier continuous
6 | Slope of waste and vent lines verified
7 | Cleanouts located and accessible
8 | Backflow prevention device installed per DEP requirements
9 | Hydrostatic / air test on domestic water complete and recorded
10 | Waste and vent test complete and recorded
11 | DOB plumbing rough inspection passed (HOLD POINT before cover)
12 | Gas piping material, sizing and support per code
13 | Gas pressure test at 10 psi for 15 min minimum, DOB witnessed
14 | Gas Activation Notice obtained from utility
15 | 4x Rheem tankless water heaters installed per manufacturer
16 | ST-120 storage tank installed, piped and insulated
17 | Combustion air and venting per manufacturer and code
18 | Combustion test performed; DOB Boiler Unit inspection arranged
19 | Recirculation and mixing valve set points verified and recorded
20 | Pool make-up water connection coordinated with Owner's vendor
21 | Trench drains and floor drains set to correct elevation and slope
22 | Suitemate water extractor voltage substitution verified per RFI
23 | Fixtures set level, sealed and operating; ADA heights verified
24 | Pipe labelling and valve tag chart complete
25 | DEP meter set and backflow certification filed
26 | As-builts, O&M manuals and warranties turned over
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## HVAC & Ductwork
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: HVAC & DUCTWORK
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 23 00 00 |  | D-10 / D-11 | Tier 3
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Roof / Zones A & B
CHECKLIST STATUS |  | Items | 26 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Approved submittals and coordination drawings on site
2 | Equipment matches approved submittal and Exhibit C early release
3 | Roof curbs, supports and flashing complete and water tested
4 | Vibration isolation and seismic restraints installed per detail
5 | Clearances for service and code access maintained
6 | Ductwork gauge, reinforcement and sealing class per SMACNA
7 | Duct hangers and supports per SMACNA spacing
8 | Duct insulation type and thickness per spec, vapour barrier continuous
9 | Duct pressure / leakage test complete before close-up (HOLD POINT)
10 | Fire and smoke dampers installed with correct sleeves and access
11 | Damper closure on fire alarm interface tested
12 | Refrigerant piping pressure and vacuum test complete before charge
13 | Refrigerant charge verified and recorded per manufacturer
14 | Condensate drains sloped, trapped and terminated correctly
15 | Pool dehumidifier PDU-1 installed and drained per manufacturer
16 | Corrosion-resistant materials used in pool room (Zone B)
17 | Kitchen exhaust KEF-1 and MUA-1 interlocked and tested
18 | Grease duct construction and clearances per code where applicable
19 | ERV-1 and ERV-2 filters, dampers and controls verified
20 | Controls point-to-point verification complete
21 | Vendor certified startup performed and report issued
22 | Functional performance testing complete and accepted
23 | TAB complete; airflows within ±10% of design CFM
24 | TR8 mechanical / energy special inspection signed off
25 | Filters replaced before turnover; systems clean
26 | O&M manuals, warranties and training delivered
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Fire Sprinkler
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: FIRE SPRINKLER
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 21 13 00 |  | D-04 | Tier 4
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Whole premises — 87 new heads
CHECKLIST STATUS |  | Items | 24 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Approved shop drawings and hydraulic calculations on site
2 | Head type, temperature rating and finish per approved submittal
3 | 87 new heads accounted for: concealed, recessed, upright, dry pendent
4 | Dry pendent heads used in all non-heated / freeze-risk locations
5 | Pipe material, fittings and listings per NFPA 13 and spec
6 | Hangers, seismic bracing and spacing per NFPA 13
7 | Head spacing, distance to walls and obstruction rules verified
8 | Coverage verified against final RCP and partition layout
9 | Sprinkler escutcheons and coverplates centred in ceiling tile
10 | Clearance to obstructions (ducts, lights, soffits, barrel vault) verified
11 | Sleeves and firestopping at all rated penetrations
12 | Inspector's test connection and drain provided and accessible
13 | Control valves accessible, labelled and supervised
14 | Hydrostatic test at 200 psi held 2 hrs, DOB witnessed
15 | Hydrostatic test record signed and uploaded to Procore
16 | Flow test performed; alarm signal within 90 seconds
17 | Waterflow and tamper switches wired and supervised at FACP
18 | FDNY field acceptance test passed
19 | Standpipe / riser signage legible and accurate
20 | Hydraulic design nameplate installed at riser
21 | Spare head cabinet with wrench and spare heads provided
22 | TR1 special inspection signed off
23 | Contractor's material and test certificate issued
24 | As-builts, O&M and warranty turned over
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date

## Fire Alarm
SAUNALOUNGE — QUALITY CONTROL CHECKLIST: FIRE ALARM
PROJECT |  | JOB NUMBER |  | DOB JOB NUMBER |  | CSI CODE |  | DFOW REF | DFOW RISK TIER
SaunaLounge — 45 South 3rd Street, Ground Floor, Brooklyn NY 11249 | [5 empty] | 28 31 00 |  | D-03 | Tier 4
LOCATION / ZONE |  | SUBCONTRACTOR |  | FOREMAN |  | PHASE OF CONTROL |  | INSPECTED BY | INSPECTION DATE
Whole premises — FACP / RAN
CHECKLIST STATUS |  | Items | 28 | Pass | 0 | Fail | 0 | % Complete | 0%
# | Checklist Item | Req'd | Rec'd | Prepped | Installed | Result | Date | Inspected By | Photo Ref | Comments / Corrective Action
1 | Approved shop drawings, riser diagram and device layout on site
2 | FDNY / DOB drawing approval obtained before installation
3 | Device type and model match approved submittal
4 | FACP and RAN locations per approved drawings and accessible
5 | Battery calculations and standby capacity verified
6 | Conduit, wiring type and class per NFPA 72 and spec
7 | Wiring segregated from power circuits per code
8 | Pre-cover inspection of rough-in signed off (HOLD POINT)
9 | Device mounting heights per NFPA 72 and ADA
10 | Smoke detector spacing and proximity to diffusers verified
11 | Detectors in pool room / high-humidity areas correct type
12 | Heat detectors in kitchen and mechanical spaces per design
13 | Notification appliance candela settings and audibility verified
14 | Strobe synchronisation verified
15 | Duct smoke detectors installed and accessible for service
16 | HVAC damper closure interface tested on alarm
17 | Door hold-open device release interface tested on alarm
18 | Sprinkler waterflow and tamper supervision verified at FACP
19 | Elevator recall — N/A (no elevator scope on this project)
20 | Device labelling and zone schedule complete and accurate
21 | 100% pre-test of all initiating, signaling and notification devices
22 | Pre-test report signed by subcontractor before FDNY witness
23 | All pre-test deficiencies corrected and re-tested; zero open NCRs
24 | Central station account active; signal transmission verified
25 | FDNY witness / acceptance test passed
26 | FDNY Letter of Approval (LOA) received and archived
27 | TR1 special inspection signed off
28 | Owner training delivered; O&M, as-builts and warranty turned over
Q-TEAM SIGN-OFF — All Fail items must be closed via the NCR Log before this checklist is signed. File in Procore.
Superintendent (Affect Build) |  |  | Trade Foreman |  |  | Architect / Owner's Rep |  |  | Date